## TL_Geometry
code | structure_type | company | state | n_circuits | n_ground_w | voltage_kv | Creep_Dist_mm_kv | Insul_Creep_Dist_mm | Insul_Spac_mm | L_Ins_String_ft | ha1t_ft | hb1t_ft | hc1t_ft | Sa1t_ft | Sb1t_ft | Sc1t_ft | hg11t_ft | Sg11t_ft | hg21t_ft | Sg21t_ft | ha2t_ft | hb2t_ft | hc2t_ft | Sa2t_ft | Sb2t_ft | Sc2t_ft | ha1 (ft) | ha1 (inch) | hb1 (ft) | hb1 (inch) | hc1 (ft) | hc1 (inch) | Sa1 (ft) | Sa1 (inch) | Sb1 (ft) | Sb1 (inch) | Sc1 (ft) | Sc1 (inch) | hg11 (ft) | hg11 (inch) | Sg11 (ft) | Sg11 (inch) | hg21 (ft) | hg21 (inch) | Sg21 (ft) | Sg21 (inch) | ha2 (ft) | ha2 (inch) | hb2 (ft) | hb2 (inch) | hc2 (ft) | hc2 (inch) | Sa2 (ft) | Sa2 (inch) | Sb2 (ft) | Sb2 (inch) | Sc2 (ft) | Sc2 (inch)
3L1 | Lattice | Iowa Public Service Co | Iowa | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -23.75 | 0 | 23.75 | 87.5 | -17.8125 | 87.5 | 17.8125 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -23 | -9 | 0 | 0 | 23 | 9 | 87 | 6 | -17.25 | -6.75 | 87 | 6 | 17.25 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L2 | Lattice | Indianapolis Power and Light Company, Western Power Area Administration | Indiana, Colorado, Colorado | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -32 | 0 | 32 | 96.5 | -21.5 | 96.5 | 21.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -32 | 0 | 0 | 0 | 32 | 0 | 96 | 6 | -21 | -6 | 96 | 6 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L3 | Lattice | Consumers Power Company | Michigan | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 59.1594 | 59.1594 | -24.5 | 0 | 24.5 | 87.5 | -16.5 | 87.5 | 16.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | -24 | -6 | 0 | 0 | 24 | 6 | 87 | 6 | -16 | -6 | 87 | 6 | 16 | 6
3L4 | Lattice | Pennsylvania Electric Co | Pennsylvania | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.1594 | 44.1594 | 44.1594 | -22.6667 | 0 | 22.6667 | 73 | -18.5833 | 73 | 18.5833 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 0 | 55 | 0 | 55 | 0 | -22 | -8 | 0 | 0 | 22 | 8 | 73 | 0 | -18 | -7 | 73 | 0 | 18 | 7
3L5 | Lattice | Northern Indiana Public Service | Indiana | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 79.1594 | 79.1594 | 79.1594 | -24 | 0 | 24 | 102 | -21.6 | 102 | 21.6 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 90 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 102 | 0 | -21.6 | 0 | 102 | 0 | 21.6 | 0
3L6 | Lattice | Cleveland electric iluminating | Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 43.6594 | 43.6594 | 43.6594 | -23 | 0 | 23 | 94.5 | -20.5 | 94.5 | 20.5 | 72.1594 | 72.1594 | 72.1594 | 23 | 0 | -23 | 54 | 6 | 54 | 6 | 54 | 6 | -23 | 0 | 0 | 0 | 23 | 0 | 93 | 18 | -20 | -6 | 93 | 18 | 20 | 6 | 82 | 12 | 82 | 12 | 82 | 12 | 23 | 0 | 0 | 0 | -23 | 0
3L7 | Lattice | Consolidated Edison Co | New York | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 41.826 | 64.826 | 87.826 | -19 | -17.5 | -15.3333 | 104.6667 | -12 | 104.6667 | 12 | 87.826 | 64.826 | 41.826 | 15.3333 | 17.5 | 19 | 52 | 8 | 75 | 8 | 98 | 8 | -19 | 0 | -17 | -6 | -15 | -4 | 104 | 8 | -12 | 0 | 104 | 8 | 12 | 0 | 98 | 8 | 75 | 8 | 52 | 8 | 15 | 4 | 17 | 6 | 19 | 0
3L8 | Lattice | Oklahoma Gas & Electric Co, American Electric Power Co | Michigan, Oklahoma | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 93.1594 | 117.1594 | -22 | -37 | -22 | 142 | -11 | 142 | 11 | 117.1594 | 93.1594 | 69.1594 | 22 | 37 | 22 | 80 | 0 | 104 | 0 | 128 | 0 | -22 | 0 | -37 | 0 | -22 | 0 | 142 | 0 | -11 | 0 | 142 | 0 | 11 | 0 | 128 | 0 | 104 | 0 | 80 | 0 | 22 | 0 | 37 | 0 | 22 | 0
3L9 | Lattice | Consumers Power Company, Indianapolis Power and Light Company | Michigan, Michigan, Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 89.1594 | 111.1594 | -18 | -29 | -17 | 137 | -24 | 137 | 24 | 111.1594 | 89.1594 | 69.1594 | 17 | 29 | 18 | 80 | 0 | 100 | 0 | 122 | 0 | -18 | 0 | -29 | 0 | -17 | 0 | 137 | 0 | -24 | 0 | 137 | 0 | 24 | 0 | 122 | 0 | 100 | 0 | 80 | 0 | 17 | 0 | 29 | 0 | 18 | 0
3L10 | Lattice | Detroit Edison | Michigan | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 53.1594 | 74.6594 | 98.6594 | -20.5 | -27 | -18.5 | 119.5 | -25.75 | 119.5 | 25.75 | 98.6594 | 74.6594 | 53.1594 | 18.5 | 27 | 20.5 | 64 | 0 | 85 | 6 | 109 | 6 | -20 | -6 | -27 | 0 | -18 | -6 | 119 | 6 | -25 | -9 | 119 | 6 | 25 | 9 | 109 | 6 | 85 | 6 | 64 | 0 | 18 | 6 | 27 | 0 | 20 | 6
3L11 | Lattice | Boston Edison Company, Consolidated Edison Co of New York, Houston Lightning Company | Massachusetts, New York, Texas, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 39.1594 | 61.1594 | 83.1594 | -25 | -25 | -25 | 98.5 | -18 | 98.5 | 18 | 83.1594 | 61.1594 | 39.1594 | -25 | -25 | -25 | 50 | 0 | 72 | 0 | 94 | 0 | -25 | 0 | -25 | 0 | -25 | 0 | 98 | 6 | -18 | 0 | 98 | 6 | 18 | 0 | 94 | 0 | 72 | 0 | 50 | 0 | -25 | 0 | -25 | 0 | -25 | 0
3L12 | Lattice | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 61.6594 | 89.6594 | 117.6594 | -15 | -20 | -15 | 136 | -9 | 136 | 9 | 117.6594 | 89.6594 | 61.6594 | 15 | 20 | 15 | 72 | 6 | 100 | 6 | 128 | 6 | -15 | 0 | -20 | 0 | -15 | 0 | 136 | 0 | -9 | 0 | 136 | 0 | 9 | 0 | 128 | 6 | 100 | 6 | 72 | 6 | 15 | 0 | 20 | 0 | 15 | 0
3L13 | Lattice | Union electric company | Missouri | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 91.1594 | 65.1594 | 65.1594 | -17.6667 | -37 | -17 | 109 | -23.3333 | 109 | 23.3333 | 91.1594 | 65.1594 | 65.1594 | 17.6667 | 17 | 37 | 102 | 0 | 76 | 0 | 76 | 0 | -17 | -8 | -37 | 0 | -17 | 0 | 109 | 0 | -23 | -4 | 109 | 0 | 23 | 4 | 102 | 0 | 76 | 0 | 76 | 0 | 17 | 8 | 17 | 0 | 37 | 0
3L14 | Lattice | Texas electric service & Light Co | Texas, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 77.1594 | 52.1594 | 52.1594 | -25.5833 | -37.8333 | -14.3333 | 103 | -15.6667 | 103 | 15.6667 | 77.1594 | 52.1594 | 52.1594 | 25.5833 | 14.3333 | 37.8333 | 88 | 0 | 63 | 0 | 63 | 0 | -25 | -7 | -37 | -10 | -14 | -4 | 103 | 0 | -15 | -8 | 103 | 0 | 15 | 8 | 88 | 0 | 63 | 0 | 63 | 0 | 25 | 7 | 14 | 4 | 37 | 10
3L15 | Lattice | Commonwealth Edison Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 97.1594 | 54.1594 | 54.1594 | -28.5 | -40.5 | -16.5 | 117 | -40.5 | 117 | 40.5 | 97.1594 | 54.1594 | 54.1594 | 69 | 16.5 | 81 | 108 | 0 | 65 | 0 | 65 | 0 | -28.5 | 0 | -40.5 | 0 | -16.5 | 0 | 117 | 0 | -40.5 | 0 | 117 | 0 | 40.5 | 0 | 108 | 0 | 65 | 0 | 65 | 0 | 69 | 0 | 16.5 | 0 | 81 | 0
3P1 | Pole | Dayton Power & Light company | Ohio | 1 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 64.1594 | 75.6594 | 87.1594 | 9 | -9 | 9 | 131.5 | 0 | 0 | 0 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 75 | 0 | 86 | 6 | 98 | 0 | 9 | 0 | -9 | 0 | 9 | 0 | 131 | 6 | 0 | 0 | 0 | 0 | 0 | 0
3P2 | Pole | Cleveland electric iluminating, Indianapolis Power and Light Company, Northeast Utilities | Ohio, Indiana, Connecticut | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 54.1594 | 77.1594 | 100.1594 | -15 | -15 | -15 | 132 | -14 | 132 | 14 | 100.1594 | 77.1594 | 54.1594 | 15 | 15 | 15 | 65 | 0 | 88 | 0 | 111 | 0 | -15 | 0 | -15 | 0 | -15 | 0 | 132 | 0 | -14 | 0 | 132 | 0 | 14 | 0 | 111 | 0 | 88 | 0 | 65 | 0 | 15 | 0 | 15 | 0 | 15 | 0
3P3 | Pole | Northern States Power Company, Wisconsin Electric Power Co | Minnesota, Wisconsin | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 90.1594 | 115.1594 | -14.25 | -21.25 | -14.25 | 135 | -17 | 135 | 17 | 115.1594 | 90.1594 | 65.1594 | 14.25 | 21.25 | 14.25 | 76 | 0 | 101 | 0 | 126 | 0 | -14 | -3 | -21 | -3 | -14 | -3 | 135 | 0 | -17 | 0 | 135 | 0 | 17 | 0 | 126 | 0 | 101 | 0 | 76 | 0 | 14 | 3 | 21 | 3 | 14 | 3
3P4 | Pole | Consolidated Edison Co, Houston Lightning Company, SouthWestern electric company | New York, Texas, Louisiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 81.1594 | 97.1594 | -11 | -11 | -11 | 111.5 | -8 | 111.5 | 8 | 97.1594 | 81.1594 | 65.1594 | 11 | 11 | 11 | 76 | 0 | 92 | 0 | 108 | 0 | -11 | 0 | -11 | 0 | -11 | 0 | 111 | 6 | -8 | 0 | 111 | 6 | 8 | 0 | 108 | 0 | 92 | 0 | 76 | 0 | 11 | 0 | 11 | 0 | 11 | 0
3P5 | Pole | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 72 | 97 | 122 | -11 | -19 | -11 | 140 | -7 | 140 | 7 | 122 | 97 | 72 | 11 | 19 | 11 | 82.8406 | 0 | 107.8406 | 0 | 132.8406 | 0 | -11 | 0 | -19 | 0 | -11 | 0 | 140 | 0 | -7 | 0 | 140 | 0 | 7 | 0 | 132.8406 | 0 | 107.8406 | 0 | 82.8406 | 0 | 11 | 0 | 19 | 0 | 11 | 0
3P6 | Pole | Dayton Power & Light company | Ohio | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 81.6594 | 104.1594 | -9 | -13 | -9 | 145.5 | 0 | 0 | 0 | 104.1594 | 81.6594 | 59.1594 | 9 | 13 | 9 | 70 | 0 | 92 | 6 | 114 | 12 | -9 | 0 | -13 | 0 | -9 | 0 | 144 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 12 | 92 | 6 | 70 | 0 | 9 | 0 | 13 | 0 | 9 | 0
3P7 | Pole | Illinois Power Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.826 | 80.826 | 80.826 | -15.5 | -41 | -16 | 127.6667 | -30 | 127.6667 | 30 | 116.826 | 80.826 | 80.826 | 15.5 | 16 | 41 | 127 | 8 | 91 | 8 | 91 | 8 | -15 | -6 | -41 | 0 | -16 | 0 | 127 | 8 | -30 | 0 | 127 | 8 | 30 | 0 | 127 | 8 | 91 | 8 | 91 | 8 | 15 | 6 | 16 | 0 | 41 | 0
3P8 | Pole | Commonwealth Edison Company | Illinois | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 98.1594 | 55.1594 | 55.1594 | -22 | -33 | -10 | 118 | 0 | 0 | 0 | 98.1594 | 55.1594 | 55.1594 | 22 | 10 | 33 | 109 | 0 | 66 | 0 | 66 | 0 | -22 | 0 | -33 | 0 | -10 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 66 | 0 | 66 | 0 | 22 | 0 | 10 | 0 | 33 | 0
3H1 | H frame | Public Service Company of New Hampshire | New Hampshire, New Hampshire | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -18 | 0 | 18 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -18 | 0 | 0 | 0 | 18 | 0 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H2 | H frame | Utah Power and Light Company | Utah | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 62.1594 | 62.1594 | 62.1594 | -27 | 0 | 27 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 73 | 0 | 73 | 0 | 73 | 0 | -26 | -12 | 0 | 0 | 26 | 12 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H3 | H frame | Niagara Mohawk Power Corporation, Illinois Power Company, Central Maine Power Co | Maine, Illinois, New York | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.826 | 44.826 | 44.826 | -26 | 0 | 26 | 65.5 | -13 | 65.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 8 | 55 | 8 | 55 | 8 | -26 | 0 | 0 | 0 | 26 | 0 | 64 | 18 | -13 | 0 | 64 | 18 | 13 | 0
3H4 | H frame | Public Service Company of New Hampshire, Northeast Utilities, New York State Electric & Gas, Vermont Electric Company, Wisconsin Public Service Corp | New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 50.1594 | 50.1594 | 50.1594 | -26 | 0 | 26 | 73.5 | -13 | 73.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 61 | 0 | 61 | 0 | 61 | 0 | -26 | 0 | 0 | 0 | 26 | 0 | 73.5 | 0 | -13 | 0 | 73.5 | 0 | 13 | 0
3H5 | H frame | El paso electric company | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 59.1594 | 52.6594 | -27 | 0 | 27 | 78 | -13.5 | 78 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 69 | 12 | 63 | 6 | -26 | -12 | 0 | 0 | 26 | 12 | 77 | 12 | -13.5 | 0 | 77 | 12 | 13.5 | 0
3H6 | H frame | Northern States Power Company, Wisconsin Electric Power Co, Kansas Gas & Electric Co | Kansas, Minnesota | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 46.6594 | 58.1594 | 46.6594 | -28.25 | 0 | 28.25 | 69 | -15.25 | 69 | 15.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 57 | 6 | 68 | 12 | 57 | 6 | -28 | -3 | 0 | 0 | 28 | 3 | 68 | 12 | -15 | -3 | 68 | 12 | 15 | 3
3H7 | H frame | Public Service Company of New Mexico | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -23.5 | 0 | 23.5 | 68.5 | -13.5 | 68.5 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -23 | -6 | 0 | 0 | 23 | 6 | 68 | 6 | -13.5 | 0 | 68 | 6 | 13.5 | 0
3H8 | H frame | Union electric company | Missouri | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 51.1594 | 51.1594 | 51.1594 | -24 | 0 | 24 | 72.5 | -26 | 72.5 | 26 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 62 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 72 | 6 | -26 | 0 | 72 | 6 | 26 | 0
3H9 | H frame | New Englad Electric System | New Hampshire | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 52.6594 | 52.6594 | -20 | 0 | 20 | 74.5 | -9.5 | 74.5 | 9.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 63 | 6 | 63 | 6 | -19 | -12 | 0 | 0 | 19 | 12 | 74 | 6 | -9 | -6 | 74 | 6 | 9 | 6
3H10 | H frame | Boston Edison Company | Massachusetts | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 96 | 70 | 70 | -10 | -32.75 | -10 | 111 | -27.25 | 111 | 27.25 | 96 | 70 | 70 | 10 | 10 | 32.75 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | -10 | 0 | -32 | -9 | -10 | 0 | 111 | 0 | -27 | -3 | 111 | 0 | 27 | 3 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | 10 | 0 | 10 | 0 | 32 | 9
3Y1 | Y | Tucson Gas & Electric Co | Arizona | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 109.2427 | 84.6594 | 84.6594 | 0 | -15 | 15 | 120.0833 | -13.5 | 120.0833 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 119 | 13 | 95 | 6 | 95 | 6 | 0 | 0 | -15 | 0 | 15 | 0 | 119 | 13 | -13.5 | 0 | 119 | 13 | 13.5 | 0
3Y2 | Y | Pacific Power Light corp | Wyoming | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -13.5 | 13.5 | 127 | -10 | 127 | 10 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -13 | -6 | 13 | 6 | 127 | 0 | -10 | 0 | 127 | 0 | 10 | 0
3Y3 | Y | SouthWestern electric company | Louisiana, Louisiana | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -19.8333 | 19.8333 | 127 | -9 | 127 | 9 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -19.5 | -4 | 19.5 | 4 | 127 | 0 | -9 | 0 | 127 | 0 | 9 | 0
5L1 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 96.7889 | 69.2889 | 69.2889 | 0 | -20 | 20 | 122.25 | -13 | 122.25 | 13 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 112 | 6 | 85 | 0 | 85 | 0 | 0 | 0 | -20 | 0 | 20 | 0 | 121 | 15 | -13 | 0 | 121 | 15 | 13 | 0
5L2 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 98.2889 | 69.2889 | 69.2889 | 0 | -15.3333 | 15.3333 | 121 | -12 | 121 | 12 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 114 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -15 | -4 | 15 | 4 | 121 | 0 | -12 | 0 | 121 | 0 | 12 | 0
5L3 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 90.2889 | 74.2889 | 74.2889 | 0 | -29 | 29 | 106 | -15 | 106 | 15 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 106 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | -29 | 0 | 29 | 0 | 106 | 0 | -15 | 0 | 106 | 0 | 15 | 0
5L4 | Lattice | Basin Electric Power Co-op | California, North Dakota, South Dakota, Colorado, Montana, New Mexico, Wyoming, Minnesota, Iowa | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 85 | 69.2889 | 69.2889 | 0 | -28 | 28 | 99 | -26 | 99 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 100.7111 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -28 | 0 | 28 | 0 | 99 | 0 | -26 | 0 | 99 | 0 | 26 | 0
5L5 | Lattice | Carolina Power & Light Co | North Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 105 | 89.2889 | 89.2889 | 0 | -30.25 | 30.25 | 122.5 | -15.5 | 122.5 | 15.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120.7111 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -30 | -3 | 30 | 3 | 122 | 6 | -15.5 | 0 | 122 | 6 | 15.5 | 0
5L6 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 64.2889 | 64.2889 | 64.2889 | 0 | -35 | 35 | 95 | -25 | 95 | 25 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 95 | 0 | -25 | 0 | 95 | 0 | 25 | 0
5L7 | Lattice | Alabama Power Company, Baltimore Gas and Electric Company | Alabama, Maryland, | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -34 | 34 | 124 | -31 | 124 | 31 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -34 | 0 | 34 | 0 | 124 | 0 | -31 | 0 | 124 | 0 | 31 | 0
5L8 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -33 | 33 | 129 | -20 | 129 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -33 | 0 | 33 | 0 | 129 | 0 | -20 | 0 | 129 | 0 | 20 | 0
5L9 | Lattice | American Electric Power Co, Arizona Public Service Co, Duke Power Company | Virginia, Arizona, South Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 79.2889 | 79.2889 | 79.2889 | 0 | -32 | 32 | 109 | -24 | 109 | 24 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 0 | 0 | -32 | 0 | 32 | 0 | 109 | 0 | -24 | 0 | 109 | 0 | 24 | 0
5L10 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -35 | 35 | 137 | -26 | 137 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 137 | 0 | -26 | 0 | 137 | 0 | 26 | 0
5L11 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 100.2889 | 131.2889 | -15 | -25 | -15 | 172 | 0 | 0 | 0 | 131.2889 | 100.2889 | 69.2889 | 15 | 25 | 15 | 85 | 0 | 116 | 0 | 147 | 0 | -15 | 0 | -25 | 0 | -15 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 116 | 0 | 85 | 0 | 15 | 0 | 25 | 0 | 15 | 0
5L12 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 114.2889 | 69.2889 | 69.2889 | -27.75 | -40.5 | -15 | 150 | -18.5 | 150 | 18.5 | 114.2889 | 69.2889 | 69.2889 | 27.75 | 15 | 40.5 | 130 | 0 | 85 | 0 | 85 | 0 | -27 | -9 | -40 | -6 | -15 | 0 | 150 | 0 | -18.5 | 0 | 150 | 0 | 18.5 | 0 | 130 | 0 | 85 | 0 | 85 | 0 | 27 | 9 | 15 | 0 | 40 | 6
5L13 | Lattice |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 112.2889 | 74.2889 | 74.2889 | -18.5 | -46.5 | -18.5 | 140 | -12.125 | 140 | 15.125 | 112.2889 | 74.2889 | 74.2889 | 18.5 | 18.5 | 46.5 | 128 | 0 | 90 | 0 | 90 | 0 | -18 | -6 | -46 | -6 | -18 | -6 | 140 | 0 | -12 | -1.5 | 140 | 0 | 15 | 1.5 | 128 | 0 | 90 | 0 | 90 | 0 | 18 | 6 | 18 | 6 | 46 | 6
5L14 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | -42 | 0 | 42 | 128 | -21.8333 | 128 | 21.8333 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -42 | 0 | 0 | 0 | 42 | 0 | 128 | 0 | -21 | -10 | 128 | 0 | 21 | 10
5P1 | Pole |  |  | 1 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 99.2889 | 129.2889 | 18 | 21 | 18 | 160 | 4 | 0 | 0 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 85 | 0 | 115 | 0 | 145 | 0 | 18 | 0 | 21 | 0 | 18 | 0 | 160 | 0 | 4 | 0 | 0 | 0 | 0 | 0
5P2 | Pole |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 60.7056 | 73.2889 | 85.7056 | 18 | -17 | 18 | 120 | -10 | 120 | 10 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 77 | -7 | 90 | -12 | 102 | -7 | 18 | 0 | -17 | 0 | 18 | 0 | 120 | 0 | -10 | 0 | 120 | 0 | 10 | 0
5H1 | H frame | Baltimore Gas and Electric Company, Baltimore Gas and Electric Company | Maryland, Maryland | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 104.2889 | 104.2889 | 104.2889 | -35 | 0 | 35 | 129 | -26 | 129 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | -35 | 0 | 0 | 0 | 35 | 0 | 129 | 0 | -26 | 0 | 129 | 0 | 26 | 0
5H2 | H frame |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 123 | 87 | 87 | -30 | -45 | -15 | 149 | -32 | 149 | 32 | 123 | 87 | 87 | 15 | 45 | 15 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | -30 | 0 | -45 | 0 | -15 | 0 | 149 | 0 | -32 | 0 | 149 | 0 | 32 | 0 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | 15 | 0 | 45 | 0 | 15 | 0
5Y1 | Y |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 106.25 | 139.25 | 106.25 | -21.5 | 0 | 21.5 | 153 | -13.75 | 153 | 13.75 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 122.7111 | -9 | 155.7111 | -9 | 122.7111 | -9 | -21 | -6 | 0 | 0 | 21 | 6 | 153 | 0 | -13 | -9 | 153 | 0 | 13 | 9
5Y2 | Y | Arkansas Power & Light Co. | Arkansas | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 118.5 | 88 | 88 | 0 | -21.5 | 21.5 | 131.5 | -20 | 131.5 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 133.7111 | 6 | 103.7111 | 0 | 103.7111 | 0 | 0 | 0 | -21 | -6 | 21 | 6 | 131 | 6 | -20 | 0 | 131 | 6 | 20 | 0
5Y3 | Y | Alabama Power Company | Alabama | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 151.25 | 126 | 126 | 0 | -21 | 21 | 165.25 | -17.5 | 165.25 | 17.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 166.7111 | 3 | 141.7111 | 0 | 141.7111 | 0 | 0 | 0 | -21 | 0 | 21 | 0 | 165 | 3 | -17 | -6 | 165 | 3 | 17 | 6
7L1 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 92 | 92 | 92 | -44.5 | 0 | 44.5 | 127 | -36 | 127 | 36 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 115.0953 | 0 | 115.0953 | 0 | 115.0953 | 0 | -44 | -6 | 0 | 0 | 44 | 6 | 127 | 0 | -36 | 0 | 127 | 0 | 36 | 0
7L2 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 86.9047 | 86.9047 | 86.9047 | -45 | 0 | 45 | 138.6667 | -50 | 138.6667 | 50 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -45 | 0 | 0 | 0 | 45 | 0 | 138 | 8 | -50 | 0 | 138 | 8 | 50 | 0
7L3 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 135 | 135 | 135 | -41.8333 | 0 | 41.8333 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 158.0953 | 0 | 158.0953 | 0 | 158.0953 | 0 | -41 | -10 | 0 | 0 | 41 | 10 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7P1 | Pole |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 100.9047 | 100.9047 | 100.9047 | -39.3333 | 0 | 39.3333 | 145 | -66 | 145 | 66 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 124 | 0 | 124 | 0 | 124 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 145 | 0 | -66 | 0 | 145 | 0 | 66 | 0
7H1 | H frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 131 | 131 | 131 | -50 | 0 | 50 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 154.0953 | 0 | 154.0953 | 0 | 154.0953 | 0 | -50 | 0 | 0 | 0 | 50 | 0 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7V1 | V frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 110 | 110 | 110 | -39.3333 | 0 | 39.3333 | 150 | -30 | 150 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 133.0953 | 0 | 133.0953 | 0 | 133.0953 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 150 | 0 | -30 | 0 | 150 | 0 | 30 | 0
EX_K4_1 | Pole | Example | Example | 1 | 1 | 33 | 0 | 0 | 0 | 0 | 29 | 29 | 29 | -4 | -1.5 | 3 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 29 | 0 | 29 | 0 | -4 | 0 | -1 | -6 | 3 | 0 | 25 | 0 | 0 | 0
DC1 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0
DC2 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0

## Neighboring
number | state | abreviation | bordering_states | n_bordering_states
1 | Alabama | AL | Mississippi, Tennessee, Florida, Georgia | 4
2 | Alaska | AK | None | 0
3 | Arizona | AZ | Nevada, New Mexico, Utah, California, Colorado | 5
4 | Arkansas | AR | Oklahoma, Tennessee, Texas, Louisiana, Mississippi, Missouri | 6
5 | California | CA | Oregon, Arizona, Nevada | 3
6 | Colorado | CO | New Mexico, Oklahoma, Utah, Wyoming, Arizona, Kansas, Nebraska | 7
7 | Connecticut | CT | New York, Rhode Island, Massachusetts | 3
8 | Delaware | DE | New Jersey, Pennsylvania, Maryland | 3
9 | Florida | FL | Georgia, Alabama | 2
10 | Georgia | GA | North Carolina, South Carolina, Tennessee, Alabama, Florida | 5
11 | Hawaii | HI | None | 0
12 | Idaho | ID | Utah, Washington, Wyoming, Montana, Nevada, Oregon | 6
13 | Illinois | IL | Kentucky, Missouri, Wisconsin, Indiana, Iowa, Michigan (water border only) | 6
14 | Indiana | IN | Michigan, Ohio, Illinois, Kentucky | 4
15 | Iowa | IA | Nebraska, South Dakota, Wisconsin, Illinois, Minnesota, Missouri | 6
16 | Kansas | KS | Nebraska, Oklahoma, Colorado, Missouri | 4
17 | Kentucky | KY | Tennessee, Virginia, West Virginia, Illinois, Indiana, Missouri, Ohio | 7
18 | Louisiana | LA | Texas, Arkansas, Mississippi | 3
19 | Maine | ME | New Hampshire | 1
20 | Maryland | MD | Virginia, West Virginia, Delaware, Pennsylvania | 4
21 | Massachusetts | MA | New York, Rhode Island, Vermont, Connecticut, New Hampshire | 5
22 | Michigan | MI | Ohio, Wisconsin, Illinois, Indiana, Minnesota (water border) | 5
23 | Minnesota | MN | North Dakota, South Dakota, Wisconsin, Iowa, Michigan (water border) | 5
24 | Mississippi | MS | Louisiana, Tennessee, Alabama, Arkansas | 4
25 | Missouri | MO | Nebraska, Oklahoma, Tennessee, Arkansas, Illinois, Iowa, Kansas, Kentucky | 8
26 | Montana | MT | South Dakota, Wyoming, Idaho, North Dakota | 4
27 | Nebraska | NE | Missouri, South Dakota, Wyoming, Colorado, Iowa, Kansas, | 6
28 | Nevada | NV | Idaho, Oregon, Utah, Arizona, California | 5
29 | New Hampshire | NH | Vermont, Maine, Massachusetts | 3
30 | New Jersey | NJ | Pennsylvania, Delaware, New York | 3
31 | New Mexico | NM | Oklahoma, Texas, Utah, Arizona, Colorado | 5
32 | New York | NY | Pennsylvania, Rhode Island (water border), Vermont, Connecticut, Massachusetts, New Jersey | 6
33 | North Carolina | NC | Tennessee, Virginia, Georgia, South Carolina | 4
34 | North Dakota | ND | South Dakota, Minnesota, Montana | 3
35 | Ohio | OH | Michigan, Pennsylvania, West Virginia, Indiana, Kentucky | 5
36 | Oklahoma | OK | Missouri, New Mexico, Texas, Arkansas, Colorado, Kansas | 6
37 | Oregon | OR | Nevada, Washington, California, Idaho | 4
38 | Pennsylvania | PA | New York, Ohio, West Virginia, Delaware, Maryland, New Jersey | 6
39 | Rhode Island | RI | Massachusetts, New York (water border), Connecticut | 3
40 | South Carolina | SC | North Carolina, Georgia, | 2
41 | South Dakota | SD | Nebraska, North Dakota, Wyoming, Iowa, Minnesota, Montana | 6
42 | Tennessee | TN | Mississippi, Missouri, North Carolina, Virginia, Alabama, Arkansas, Georgia, Kentucky | 8
43 | Texas | TX | New Mexico, Oklahoma, Arkansas, Louisiana | 4
44 | Utah | UT | Nevada, New Mexico, Wyoming, Arizona, Colorado, Idaho | 6
45 | Vermont | VT | New Hampshire, New York, Massachusetts | 3
46 | Virginia | VA | North Carolina, Tennessee, West Virginia, Kentucky, Maryland | 5
47 | Washington | WA | Oregon, Idaho | 2
48 | West Virginia | WV | Pennsylvania, Virginia, Kentucky, Maryland, Ohio | 5
49 | Wisconsin | WI | Michigan, Minnesota, Illinois, Iowa | 4
50 | Wyoming | WY | Nebraska, South Dakota, Utah, Colorado, Idaho, Montana | 6

## TL_dataset
code | structure_type | company | state | miles | voltage_kv | conductor_type | conductor_name | Flag_cond_dataset | conductor_diameter_inch | conductor_kcmil | conductor_stranding | bundling | bundling_spacing_inch | ground_Type | ground_diameter_inch | ground_kcmil |  | concatenation | 3L1 | 3L2 | 3L3 | 3L4 | 3L5 | 3L6 | 3L7 | 3L8 | 3L9 | 3L10 | 3L11 | 3L12 | 3L13 | 3L14 | 3L15 | 3P1 | 3P2 | 3P3 | 3P4 | 3P5 | 3P6 | 3P7 | 3P8 | 3H1 | 3H2 | 3H3 | 3H4 | 3H5 | 3H6 | 3H7 | 3H8 | 3H9 | 3H10 | 3Y1 | 3Y2 | 3Y3 | 5L1 | 5L2 | 5L3 | 5L4 | 5L5 | 5L6 | 5L7 | 5L8 | 5L9 | 5L10 | 5L11 | 5L12 | 5L13 | 5L14 | 5P1 | 5P2 | 5H1 | 5H2 | 5Y1 | 5Y2 | 5Y3 | 7L1 | 7L2 | 7L3 | 7P1 | 7H1 | 7V1
3L8 | Lattice | American Electric Co. | Michigan | 188 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3L8: Michigan
3L11 | Lattice | Boston Edison Company | Massachusetts | 18 | 345 | ACAR | Lapwing | 1 | 1.504 | 1703 | 48/13 | 2 | 18 | Alumoweld | 0.343 | 117.649 |  | ACARLapwing | 3L11: Massachusetts
3H10 | H Frame | Boston Edison Company | Massachusetts | 33 | 345 | ACSR | Falcon | 1 | 1.545 | 1590 | 54/19 | 2 | 18 | Alumoweld | 0.343 | 117.649 |  | ACSRFalcon | 3H10: Massachusetts
3H3 | H Frame | Central Maine Power Co | Maine | 86.8 | 345 | AAC | Hawthorn | 1 | 1.1 | 1192.5 | 61/0 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | AACHawthorn | 3H3: Maine
3P2 | Pole | Cleveland Electric Iluminating Co | Ohio | 18 | 345 | ACSR | Cardinal | 1 | 1.175 | 954 | 48/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRCardinal | 3P2: Ohio
3L6 | Lattice | Cleveland Electric Iluminating Co | Ohio | 44 | 345 | ACSR | Cardinal | 1 | 1.175 | 957 | 48/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRCardinal | 3L6: Ohio
3L15 | Lattice | Commonwealth Edison Company | Illinois | 104 | 345 | ACAR | Bunting | 1 | 1.302 | 1277 | 54/7 | 2 | 18 | Alumoweld | 0.349 | 121.801 |  | ACARBunting | 3L15: Illinois
3P8 | Pole | Commonwealth Edison Company | Illinois | 54 | 345 | ACAR | Bunting | 1 | 1.302 | 1277 | 54/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACARBunting | 3P8: Illinois
3P4 | Pole | Consolidated Edison Co of New York | New York | 19 | 345 | ACAR | Kingfisher | 1 | 1.821 | 2500 | 54/37 | 2 | 18 | Alumoweld | 0.5625 | 316.4062 |  | ACARKingfisher | 3P4: New York
3L11 | Lattice | Consolidated Edison Co of New York | New York | 25 | 345 | ACAR | Kingfisher | 1 | 1.821 | 2500 | 54/37 | 2 | 18 | Alumoweld | 0.5625 | 316.4062 |  | ACARKingfisher | 3L11: New York
3L7 | Lattice | Consolidated Edison Co of New York | New York | 150 | 345 | ACSR | Kiwi | 1 | 1.82 | 2167 | 72/7 | 2 | 18 | Alumoweld | 0.5625 | 316.4062 |  | ACSRKiwi | 3L7: New York
3L3 | Lattice | Consumers Power Company | Michigan | 253 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3L3: Michigan
3L9 | Lattice | Consumers Power Company | Michigan | 377 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3L9: Michigan
3L9 | Lattice | Consumers Power Company | Michigan | 161.6 | 345 | ACSR | Bobolink | 1 | 1.427 | 1431 | 45/7 | 2 | 18 | Steel | 0.4375 | 191.4062 | 7/16 | ACSRBobolink | 3L9: Michigan
3P6 | Pole | Dayton Power & Light Company | Ohio | 24.5 | 345 | ACAR | Rail | 1 | 1.165 | 1024.5 | 30/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACARRail | 3P6: Ohio
3P1 | Pole | Dayton Power & Light Company | Ohio | 21.8 | 345 | ACAR | Rail | 1 | 1.165 | 1024.5 | 30/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACARRail | 3P1: Ohio
3L10 | Lattice | Detroit Edison | Michigan | 130 | 345 | ACSR | Bobolink | 1 | 1.427 | 1431 | 45/7 | 2 | 18 | ACSR | 0.576 | 331.776 |  | ACSRBobolink | 3L10: Michigan
3H5 | H Frame | El Paso Electric Copany | New Mexico | 230 | 345 | ACSR | Tern | 1 | 1.063 | 795 | 45/7 | 2 | 18 | Galv Steel | 0.375 | 140.625 | 3/8 | ACSRTern | 3H5: New Mexico
3P4 | Pole | Houston Lightinh & Power Company | Texas | 1.6 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3P4: Texas
3L11 | Lattice | Houston Lightinh & Power Company | Texas | 18 | 345 | ACSR | Kiwi | 1 | 1.737 | 2167 | 72/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRKiwi | 3L11: Texas
3L11 | Lattice | Houston Lightinh & Power Company | Texas | 46 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L11: Texas
3H3 | H Frame | Illinois Power Company | Illinois | 356 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Alumoweld | 0.385 | 148.225 |  | ACSRBluebird | 3H3: Illinois
3P7 | Pole | Illinois Power Company | Illinois | 15.5 | 345 | ACSR | Falcon | 1 | 1.293 | 1590 | 54/19 | 2 | 18 | Alumoweld | 0.433 | 187.489 |  | ACSRFalcon | 3P7: Illinois
3L2 | Lattice | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3L2: Indiana
3L9 | Lattice | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3L9: Indiana
3P2 | Pole | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3P2: Indiana
3L1 | Lattice | Iowa Public Service Co | Iowa | 76 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L1: Iowa
3H6 | H Frame | Kansas Gas & Electric Co | Kansas | 600 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRRail | 3H6: Kansas
3H9 | H Frame | New Englad Electric System | New Hampshire | 36 | 345 | AAC | Marigold | 1 | 1.216 | 1113 | 61/0 | 2 | 16 | Alumoweld | 0.343 | 117.649 |  | AACMarigold | 3H9: New Hampshire
3H4 | H Frame | New York State Electric & Gas | New York | 220 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3H4: New York
3H4 | H Frame | New York State Electric & Gas | New York | 56.9 | 345 | ACSR | Ortolan | 1 | 1.212 | 1033.5 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSROrtolan | 3H4: New York
3H3 | H Frame | Niagara Mohawk Power Corp. | New York | 83 | 345 | ACSR | Bunting | 1 | 1.302 | 1192.5 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRBunting | 3H3: New York
3H4 | H Frame | Northeast Utilities | Connecticut | 275 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.375 | 140.625 |  | ACSRRail | 3H4: Connecticut
3P2 | Pole | Northeast Utilities | Connecticut | 11.8 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | Alumoweld | 0.375 | 140.625 |  | ACSRBittern | 3P2: Connecticut
3L5 | Lattice | Northern Indiana Public Service Co | Indiana | 19.45 | 345 | ACSR | Bluebird | 1 | 1.762 | 3104.644 | 84/19 | 1 | 0 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3L5: Indiana
3H6 | H Frame | Northern States Power Company | Minnesota | 336.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3H6: Minnesota
3P3 | Pole | Northern States Power Company | Minnesota | 96.4 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRCardinal | 3P3: Minnesota
3L8 | Lattice | Oklahoma Gas & Electric Co. | Oklahoma | 230.9 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L8: Oklahoma
3Y2 | Y | Pacific Power & Light Co. | Wyoming | 471.2 | 345 | ACSR | Skylark | 1 | 1.316 | 1272 | 36/1 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRSkylark | 3Y2: Wyoming
3L4 | Lattice | Pennsylvania Electric Co. | Pennsylvania | 27.3 | 345 | ACSR | Curlew | 1 | 1.246 | 1033.5 | 54/7 | 2 | 18 | EHS steel | 15.5 | 240250 | 3/8 | ACSRCurlew | 3L4: Pennsylvania
3H4 | H Frame | Public Service Company of New Hampshire | New Hampshire | 23.6 | 345 | ACSR | Finch | 1 | 1.293 | 1113 | 54/19 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRFinch | 3H4: New Hampshire
3H1 | H Frame | Public Service Company of New Hampshire | New Hampshire | 17 | 345 | ACSR | Finch | 1 | 1.293 | 1113 | 54/19 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRFinch | 3H1: New Hampshire
3H1 | H Frame | Public Service Company of New Hampshire | New Hampshire | 36.4 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRBluebird | 3H1: New Hampshire
3H7 | H Frame | Public Service Co. of New Mexico | New Mexico | 160 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3H7: New Mexico
3Y3 | Y | Southwestern Electric Power Company | Louisiana | 64.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | Alumoweld | 0.433 | 187.489 |  | ACSRDrake | 3Y3: Louisiana
3P4 | Pole | Southwestern Electric Power Company | Louisiana | 7.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3P4: Louisiana
3Y3 | Y | Southwestern Electric Power Company | Louisiana | 73.4 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 54/19 | 1 | 0 | Alumoweld | 0.433 | 187.489 |  | ACSRBluebird | 3Y3: Louisiana
3L14 | Lattice | Texas Electric Service Co. | Texas | 240.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L14: Texas
3L14 | Lattice | Texas Power & Light Co. | Texas | 68.8 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRDrake | 3L14: Texas
3Y1 | Y | Tucson Gas & Electric Co. | Arizona | 413 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRRail | 3Y1: Arizona
3H8 | H Frame | Union Electric Company | Missouri | 186 | 345 | ACSR | Tern | 1 | 1.063 | 795 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRTern | 3H8: Missouri
3L13 | Lattice | Union Electric Company | Missouri | 23 | 345 | ACSR | Lapwing | 1 | 1.504 | 1590 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRLapwing | 3L13: Missouri
3L12 | Lattice | Utah Power and Light Company | Utah | 45 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | EHS steel | 0.5 | 250 | 1/2 | ACSRBittern | 3L12: Utah
3P5 | Pole | Utah Power and Light Company | Utah | 61 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | EHS steel | 0.5 | 250 | 1/2 | ACSRBittern | 3P5: Utah
3H2 | H Frame | Utah Power and Light Company | Utah | 248 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | Alumoweld | 0.475 | 225.625 |  | ACSRCardinal | 3H2: Utah
3H4 | H Frame | Vermont Electric Company | Vermont | 51.3 | 345 | ACAR | Drake | 1 | 1.108 | 927.2 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACARDrake | 3H4: Vermont
3L2 | Lattice | Western Area Power Administration | Colorado | 141 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | Steel | 0.5 | 250 |  | ACSRBittern | 3L2: Colorado
3L2 | Lattice | Western Area Power Administration | Colorado | 419 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRCardinal | 3L2: Colorado
3P3 | Pole | Wisconsin Electric Power Co | Wisconsin | 28 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | ACSR Guinea | 0.576 | 159 |  | ACSRBluebird | 3P3: Wisconsin
3H4 | H Frame | Wisconsin Public Service Corp | Wisconsin | 28.8 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3H4: Wisconsin
5L7 | Lattice | Alabama Power Company |  | 97 | 500 | ACSR |  |  | 1.213 |  | 45/7 | 3 | 18 | Alumoweld | 0.385 |  |  | ACSR | 5L7: 0
5Y3 | Y | Alabama Power Company |  | 126 | 500 | ACSR |  |  | 1.213 |  | 45/7 | 3 | 18 | Alumoweld | 0.385 |  |  | ACSR | 5Y3: 0
5L9 | Lattice | American Electric Co. |  | 117 | 500 | ACAR |  |  | 1.65 |  | 42/19 | 2 | 18 | Alumoweld | 0.385 |  |  | ACAR | 5L9: 0
5L9 | Lattice | Arizona Public Service Co. |  | 1083 | 500 | ACSR |  |  | 1.762 |  | 84/19 | 2 | 18 | Alumoweld | 0.385 |  |  | ACSR | 5L9: 0
5Y2 | Y | Arkansas Power & Light Co. |  | 109.26 | 500 | ACSR |  |  | 1.165 |  | 45/7 | 3 | 18 | Alumoweld | 0.433 |  |  | ACSR | 5Y2: 0
5L7 | Lattice | Baltimore Gas & Electric Company |  | 154.82 | 500 | ACSR |  |  | 1.821 |  | 84/19 | 2 | 18 | Alumoweld | 0.572 |  |  | ACSR | 5L7: 0
5L7 | Lattice | Baltimore Gas & Electric Company |  | 33.7 | 500 | ACSR |  |  | 1.504 |  | 45/7 | 3 | 18 | Alumoweld | 0.572 |  |  | ACSR | 5L7: 0
5L4 | Lattice | Basin Electric Power Co-op. |  | 300 | 500 | ACSR |  |  | 1.8 |  | 73/19 | 2 | 18 | EHS steel | 0.4375 |  |  | ACSR | 5L4: 0
5L12 | Lattice | Bonneville Power Administration |  | 24 | 500 | ACSR |  |  | 1.302 |  | 45/7 | 3 | 18 | Alumoweld | 0.385 |  |  | ACSR | 5L12: 0
5L2 | Lattice | Bonneville Power Administration |  | 17.3 | 500 | ACSR |  |  | 1.602 |  | 84/19 | 3 | 18 | Alumoweld | 0.386 |  |  | ACSR | 5L2: 0
5L11 | Lattice | Bonneville Power Administration |  | 151.6 | 500 | ACSR |  |  | 1.602 |  | 84/19 | 3 | 18 | Alumoweld | 0.386 |  |  | ACSR | 5L11: 0
5L5 | Lattice | Carolina Power & Light Co. |  | 88 | 500 | ACSR |  |  | 1.88 |  | 76/19 | 2 | 18 | Alumoweld | 0.433 |  |  | ACSR | 5L5: 0
5L9 | Lattice | Duke Power Company |  | 110 | 500 | ACSR |  |  | 1.88 |  | 76/19 | 2 | 18 | EHS steel | 0.5 |  |  | ACSR | 5L9: 0
5L7 | Lattice | Florida Power Corp |  | 125 | 500 | ACAR |  |  | 1.72 |  | 30/61 | 2 | 18 | Alumoweld | 0.349 |  |  | ACAR | 5L7: 0
5L10 | Lattice | General Public Utilities |  | 630 | 500 | ACAR |  |  | 1.821 |  | 54/37 | 2 | 18 | Alumoweld | 0.572 |  |  | ACAR | 5L10: 0
5L10 | Lattice | General Public Utilities |  | 74.8 | 500 | ACAR |  |  | 1.821 |  | 54/37 | 2 | 18 | Alumoweld | 0.572 |  |  | ACAR | 5L10: 0
5L7 | Lattice | Georgia Power Company |  | 861 | 500 | ACSR |  |  | 1.259 |  | 45/7 | 3 | 18 | Steel | 0.36 |  |  | ACSR | 5L7: 0
5L8 | Lattice | Gulf States Utilities Co. |  | 320 | 500 | ACAR |  |  | 1.165 |  | 24/13 | 3 | 18 | EHS steel | 0.433 |  |  | ACAR | 5L8: 0
5L6 | Lattice | Los Angeles Dept. of Water & Power |  | 237 | 500 | ACSR |  |  | 1.7 |  | 76/19 | 2 | 18 | EHS steel | 0.5 |  |  | ACSR | 5L6: 0
5L8 | Lattice | Louisiana Power & Light |  | 222 | 500 | ACAR |  |  | 1.165 |  | 24/13 | 3 | 18 | EHS steel | 0.4375 |  |  | ACAR | 5L8: 0
5Y1 | Y | Northern States Power Co. |  | 162 | 500 | ACSR |  |  | 1.302 |  | 45/7 | 3 | 18 | EHS steel | 0.4375 |  |  | ACSR | 5Y1: 0
5L14 | Lattice | Pacific Gas & Electric Co. |  | 1275 | 500 | AAC |  |  | 1.75 |  | 61/0 | 2 | 18 | Alumoweld | 0.385 |  |  | AAC | 5L14: 0
5H1 | H Frame | Pacific Power & Light Co. |  |  | 500 | ACSR |  |  | 1.602 |  | 84/19 | 2 | 18 | Alumoweld | 0.385 |  |  | ACSR | 5H1: 0
5L8 | Lattice | Pacific Power & Light Co. |  |  | 500 | ACSR |  |  | 1.316 |  | 36/1 | 3 | 18 | EHS steel | 0.375 |  |  | ACSR | 5L8: 0
5P2 | Pole | Pennsylvania Power & Light Company |  |  | 500 | ACSR |  |  | 1.504 |  | 45/7 | 3 | 18 | Alumoweld | 0.572 |  |  | ACSR | 5P2: 0
5H1 | H Frame | Pennsylvania Power & Light Company |  |  | 500 | ACAR |  |  | 1.821 |  | 54/37 | 2 | 18 | Alumoweld | 0.572 |  |  | ACAR | 5H1: 0
5H2 | H Frame | Pennsylvania Power & Light Company |  |  | 500 | ACSR |  |  | 1.504 |  | 45/7 | 3 | 18 | Alumoweld | 0.572 |  |  | ACSR | 5H2: 0
5L1 | Lattice | Portland General Electric Co. |  |  | 500 | ACSR |  |  | 1.602 |  | 84/19 | 2 | 18 | Alumoweld | 0.385 |  |  | ACSR | 5L1: 0
5H2 | H Frame | Potomac Electric Power Company |  |  | 500 | ACSR |  |  | 1.504 |  | 45/7 | 3 | 18 | Alumoweld | 0.433 |  |  | ACSR | 5H2: 0
5L13 | Lattice | Potomac Electric Power Company |  |  | 500 | ACSR |  |  | 1.504 |  | 45/7 | 3 | 18 | Alumoweld | 0.433 |  |  | ACSR | 5L13: 0
5L10 | Lattice | Public Service Electric & Gas Company |  |  | 500 | ACAR |  |  | 1.821 |  | 54/37 | 2 | 18 | Alumoweld | 0.572 |  |  | ACAR | 5L10: 0
5P1 | Pole | Public Service Electric & Gas Company |  |  | 500 | ACAR |  |  | 1.821 |  | 54/37 | 2 | 18 | Alumoweld | 0.572 |  |  | ACAR | 5P1: 0
5L9 | Lattice | Southern Calif. Edison Co. |  |  | 500 | ACSR |  |  | 1.762 |  | 84/19 | 2 | 18 | Alumoweld | 0.485 |  |  | ACSR | 5L9: 0
5L7 | Lattice | Tennessee Valley Authority |  |  | 500 | ACSR |  |  | 1.165 |  | 45/7 | 3 | 18 | Alumoweld | 0.343 |  |  | ACSR | 5L7: 0
5L3 | Lattice | Virginia Electric & Power Co. |  |  | 500 | ACAR |  |  | 1.823 |  | 84/7 | 2 | 18 | Alumoweld | 0.433 |  |  | ACAR | 5L3: 0
5L8 | Lattice | Western Area Power Administration |  |  | 500 | ACSR |  |  | 1.602 |  | 84/19 | 2 | 18 | Alumoweld | 0.433 |  |  | ACSR | 5L8: 0
7L2 | Lattice | American Electric Power Company |  |  | 765 | ACSR |  |  | 1.165 |  | 45/7 | 4 | 18 | Alumoweld | 0.385 |  |  | ACSR | 7L2: 0
7L2 | Lattice | American Electric Power Company |  |  | 765 | ACSR |  |  | 1.385 |  | 45/7 | 4 | 18 | Alumoweld | 0.385 |  |  | ACSR | 7L2: 0
7L1 | Lattice | Commonwealth Edison Company |  |  | 765 | ACAR |  |  | 1.6 |  | 36/7 | 4 | 24 | Alumoweld | 0.385 |  |  | ACAR | 7L1: 0
7H1 | H Frame | Niagara Mohawk Power Corp. |  |  | 765 | ACSR |  |  | 1.386 |  | 45/7 | 4 | 18 | EHS steel | 0.4375 |  |  | ACSR | 7H1: 0
7V1 | Lattice | Quebec Hydro Electric Commission |  |  | 735 | ACSR |  |  | 1.592 |  | 48/7 | 4 | 18 | Grade 180 Steel Glv | 0.5 |  |  | ACSR | 7V1: 0
7P1 | Pole | Quebec Hydro Electric Commission |  |  | 735 | ACSR |  |  | 1.468 |  | 48/7 | 4 | 18 | Grade 220 Steel Glv | 0.5 |  |  | ACSR | 7P1: 0
7L3 | Lattice | Quebec Hydro Electric Commission |  |  | 735 | ACSR |  |  | 1.592 |  | 48/7 | 4 | 18 | Grade 180 Steel Glv | 0.5 |  |  | ACSR | 7L3: 0
[19 empty] | Iowa | Indiana, Colorado, Colorado | Michigan | Pennsylvania | Indiana | Ohio | New York | Michigan, Oklahoma | Michigan, Michigan, Indiana | Michigan | Massachusetts, New York, Texas, Texas | Utah | Missouri | Texas, Texas | Illinois | Ohio | Ohio, Indiana, Connecticut | Minnesota, Wisconsin | New York, Texas, Louisiana | Utah | Ohio | Illinois | Illinois | New Hampshire, New Hampshire | Utah | Maine, Illinois, New York | New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin | New Mexico | Kansas, Minnesota | New Mexico | Missouri | New Hampshire | Massachusetts | Arizona | Wyoming | Louisiana, Louisiana | 0 | 0 | 0 | 0 | 0 | 0 | 0, 0, 0, 0, 0, 0 | 0, 0, 0, 0 | 0, 0, 0, 0 | 0, 0, 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0, 0 | 0, 0 | 0 | 0 | 0 | 0 | 0, 0 | 0 | 0 | 0 | 0
[19 empty] | Iowa | Indiana, Colorado, Colorado | Michigan | Pennsylvania | Indiana | Ohio | New York | Michigan, Oklahoma | Michigan, Michigan, Indiana | Michigan | Massachusetts, New York, Texas, Texas | Utah | Missouri | Texas, Texas | Illinois | Ohio | Ohio, Indiana, Connecticut | Minnesota, Wisconsin | New York, Texas, Louisiana | Utah | Ohio | Illinois | Illinois | New Hampshire, New Hampshire | Utah | Maine, Illinois, New York | New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin | New Mexico | Kansas, Minnesota | New Mexico | Missouri | New Hampshire | Massachusetts | Arizona | Wyoming | Louisiana, Louisiana
Iowa
Indiana, Colorado, Colorado
Michigan
Pennsylvania
Indiana
Ohio
New York
Michigan, Oklahoma
Michigan, Michigan, Indiana
Michigan
Massachusetts, New York, Texas, Texas
Utah
Missouri
Texas, Texas
Illinois
Ohio
Ohio, Indiana, Connecticut
Minnesota, Wisconsin
New York, Texas, Louisiana
Utah
Ohio
Illinois
Illinois
Illinois
New Hampshire, New Hampshire
Utah
Maine, Illinois, New York
New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin
New Mexico
Kansas, Minnesota
New Mexico
Missouri
New Hampshire
Massachusetts
Arizona
Wyoming
Louisiana, Louisiana

## Conductors
type | codeword | size_kcmil | stranding | diameter_inch | R_20dc_ohm_kft | R_25AC_ohm_kft | R_50AC_ohm_kft | R_75AC_ohm_kft | C_60Hz_Mohm_kft | L_60Hz_ohm_kft | ampacity_a | weight lb_kft | m_strength_kip | m_strength_kip | Concatenation
ACSR | Waxwing | 266.8 | 18/1 | 0.609 | 0.0644 | 0.0657 | 0.0723 | 0.0788 | 0.576 | 0.0903 | 445 |  |  |  | ACSRWaxwing
ACSR | Partridge | 266.8 | 26/7 | 0.642 | 0.0637 | 0.0652 | 0.0714 | 0.0778 | 0.565 | 0.0881 | 455 |  |  |  | ACSRPartridge
ACSR | Merlin | 336.4 | 18/1 | 0.684 | 0.051 | 0.0523 | 0.0574 | 0.0625 | 0.56 | 0.0826 | 515 |  |  |  | ACSRMerlin
ACSR | Linnet | 336.4 | 26/7 | 0.721 | 0.0506 | 0.0517 | 0.0568 | 0.0619 | 0.549 | 0.0854 | 530 |  |  |  | ACSRLinnet
ACSR | Oriole | 336.4 | 30/7 | 0.741 | 0.0502 | 0.0513 | 0.0563 | 0.0614 | 0.544 | 0.0843 | 530 |  |  |  | ACSROriole
ACSR | Chickadee | 397.5 | 18/1 | 0.743 | 0.0432 | 0.0443 | 0.0487 | 0.0528 | 0.544 | 0.0856 | 575 |  |  |  | ACSRChickadee
ACSR | Ibis | 397.5 | 26/7 | 0.783 | 0.0428 | 0.0438 | 0.0481 | 0.0525 | 0.539 | 0.0835 | 590 |  |  |  | ACSRIbis
ACSR | Pelican | 477 | 18/1 | 0.814 | 0.036 | 0.0369 | 0.0405 | 0.0441 | 0.528 | 0.0835 | 640 |  |  |  | ACSRPelican
ACSR | Flicker | 477 | 24/7 | 0.846 | 0.0358 | 0.0367 | 0.0403 | 0.0439 | 0.524 | 0.0818 | 670 |  |  |  | ACSRFlicker
ACSR | Hawk | 477 | 26/7 | 0.858 | 0.0357 | 0.0366 | 0.0402 | 0.0438 | 0.522 | 0.0814 | 660 |  |  |  | ACSRHawk
ACSR | Hen | 477 | 30/7 | 0.883 | 0.0354 | 0.0362 | 0.0398 | 0.0434 | 0.517 | 0.0803 | 660 |  |  |  | ACSRHen
ACSR | Osprey | 556.5 | 18/1 | 0.879 | 0.0309 | 0.0318 | 0.0348 | 0.0379 | 0.518 | 0.0818 | 710 |  |  |  | ACSROsprey
ACSR | Parakeet | 556.5 | 24/7 | 0.914 | 0.0307 | 0.0314 | 0.0347 | 0.0377 | 0.512 | 0.0801 | 720 |  |  |  | ACSRParakeet
ACSR | Dove | 556.5 | 26/7 | 0.927 | 0.0305 | 0.0314 | 0.0345 | 0.0375 | 0.51 | 0.0795 | 730 |  |  |  | ACSRDove
ACSR | Rook | 636 | 24/7 | 0.977 | 0.0268 | 0.0277 | 0.0303 | 0.033 | 0.502 | 0.0786 | 780 |  |  |  | ACSRRook
ACSR | Grosbeak | 636 | 26/7 | 0.99 | 0.0267 | 0.0275 | 0.0301 | 0.0328 | 0.499 | 0.078 | 790 |  |  |  | ACSRGrosbeak
ACSR | Drake | 795 | 26/7 | 1.108 | 0.0214 | 0.0222 | 0.0242 | 0.0263 | 0.482 | 0.0756 | 910 |  |  |  | ACSRDrake
ACSR | Tern | 795 | 45/7 | 1.063 | 0.0216 | 0.0225 | 0.0246 | 0.0267 | 0.488 | 0.0769 | 890 |  |  |  | ACSRTern
ACSR | Rail | 954 | 45/7 | 1.165 | 0.018 | 0.0188 | 0.0206 | 0.0223 | 0.474 | 0.0748 | 970 |  |  |  | ACSRRail
ACSR | Cardinal | 954 | 54/7 | 1.196 | 0.0179 | 0.0186 | 0.0205 | 0.0222 | 0.47 | 0.0737 | 990 |  |  |  | ACSRCardinal |  |  |  | 0.46951
ACSR | Ortolan | 1033.5 | 45/7 | 1.213 | 0.0167 | 0.0175 | 0.019148 | 0.021 | 0.46728 | 0.073864 | 1030 |  |  |  | ACSROrtolan | From Stevenson |  | from prioritywire catalog | 0.4673
ACSR | Curlew | 1033.5 | 54/7 | 1.246 | 0.0165 | 0.0172 | 0.0189 | 0.0205 | 0.464 | 0.0729 | 1040 |  |  |  | ACSRCurlew | Not in ASTM B232 |  |  | 0.4631
ACSR | Bluejay | 1113 | 45/7 | 1.259 | 0.0155 | 0.0163 | 0.0178 | 0.0193 | 0.461 | 0.0731 | 1070 |  |  |  | ACSRBluejay |  |  |  | 0.46147
ACSR | Finch | 1113 | 54/19 | 1.293 | 0.0155 | 0.016212 | 0.017746 | 0.02 | 0.45725 | 0.07197 | 1070 |  |  |  | ACSRFinch | From Stevenson |  | from prioritywire catalog | 0.4573
ACSR | Bittern | 1272 | 45/7 | 1.345 | 0.0135 | 0.0144 | 0.0157 | 0.017 | 0.451 | 0.0716 | 1160 |  |  |  | ACSRBittern |  |  |  | 0.45113
ACSR | Pheasant | 1272 | 54/19 | 1.382 | 0.0135 | 0.014223 | 0.015549 | 0.017 | 0.44722 | 0.070455 | 1180 |  |  |  | ACSRPheasant | From Stevenson |  | from prioritywire catalog | 0.44688
ACSR | Bobolink | 1431 | 45/7 | 1.427 | 0.0121 | 0.012955 | 0.014129 | 0.015 | 0.44194 | 0.070265 | 1260 |  |  |  | ACSRBobolink | From Stevenson |  | from prioritywire catalog | 0.44186
ACSR | Plover | 1431 | 54/19 | 1.465 | 0.012 | 0.012746 | 0.01392 | 0.016 | 0.43771 | 0.069129 | 1270 |  |  |  | ACSRPlover | From Stevenson |  | from prioritywire catalog | 0.43775
ACSR | Lapwing | 1590 | 45/7 | 1.502 | 0.0108 | 0.0117 | 0.0128 | 0.0138 | 0.434 | 0.0689 | 1340 |  |  |  | ACSRLapwing |  |  |  | 0.43385
ACSR | Falcon | 1590 | 54/19 | 1.545 | 0.0108 | 0.0116 | 0.0129 | 0.014 | 0.43 | 0.0678 | 1360 |  |  |  | ACSRFalcon |  |  |  | 0.42943
ACSR | Bluebird | 2156 | 84/19 | 1.762 | 0.00801 | 0.00903 | 0.00977 | 0.0105 | 0.409 | 0.0652 | 1610 |  |  |  | ACSRBluebird |  |  |  | 0.40885
AAC | Laurel | 266.8 | 19/0 | 0.593 | 0.0648 | 0.0663 | 0.0727 | 0.0794 | 0.581 | 0.0648 | 445 |  |  |  | AACLaurel |  |  |  | 0.57934
AAC | Tulip | 336.4 | 19/0 | 0.666 | 0.0513 | 0.0527 | 0.0578 | 0.0629 | 0.56 | 0.0513 | 510 |  |  |  | AACTulip |  |  |  | 0.56116
AAC | Cosmos | 477 | 19/0 | 0.792 | 0.0363 | 0.0373 | 0.0409 | 0.0445 | 0.533 | 0.0363 | 640 |  |  |  | AACCosmos |  |  |  | 0.53404
AAC | Syringa | 477 | 37/0 | 0.795 | 0.0363 | 0.0373 | 0.0409 | 0.0445 | 0.533 | 0.0363 | 640 |  |  |  | AACSyringa |  |  |  | 0.53345
AAC | Zinnia | 500 | 19/0 | 0.811 | 0.0346 | 0.0356 | 0.039 | 0.0426 | 0.533 | 0.0346 | 660 |  |  |  | AACZinnia |  |  |  | 0.53033
AAC | Dahlia | 556.5 | 19/0 | 0.856 | 0.0311 | 0.032 | 0.0352 | 0.0383 | 0.522 | 0.0311 | 700 |  |  |  | AACDahlia |  |  |  | 0.52187
AAC | Orchid | 636 | 37/0 | 0.918 | 0.0272 | 0.0282 | 0.0309 | 0.0335 | 0.511 | 0.0272 | 760 |  |  |  | AACOrchid |  |  |  | 0.51092
AAC | Violet | 715 | 37/0 | 0.974 | 0.0241 | 0.025 | 0.0275 | 0.0299 | 0.502 | 0.0241 | 820 |  |  |  | AACViolet |  |  |  | 0.50165
AAC | Arbutus | 795 | 37/0 | 1.026 | 0.0217 | 0.0227 | 0.0248 | 0.0269 | 0.494 | 0.0217 | 880 |  |  |  | AACArbutus |  |  |  | 0.49351
AAC | Magnolia | 954 | 37/0 | 1.124 | 0.0181 | 0.0191 | 0.0208 | 0.0227 | 0.479 | 0.0181 | 980 |  |  |  | AACMagnolia |  |  |  | 0.47923
AAC | Bluebell | 1033.5 | 37/0 | 1.17 | 0.0167 | 0.0177 | 0.0193 | 0.021 | 0.473 | 0.0167 | 1030 |  |  |  | AACBluebell |  |  |  | 0.47295
AAC | Marigold | 1113 | 61/0 | 1.216 | 0.0155 | 0.0165 | 0.019 | 0.0195 | 0.467 | 0.0744 | 1050 |  |  |  | AACMarigold |  |  |  | 0.46691
AAC | Columbine | 1351.5 | 61/0 | 1.34 | 0.0128 | 0.0138 | 0.0151 | 0.0163 | 0.452 | 0.0128 | 1210 |  |  |  | AACColumbine |  |  |  | 0.45171
AAC | Coreopsis | 1590 | 61/0 | 1.454 | 0.0128 | 0.012 | 0.013 | 0.0141 | 0.439 | 0.0128 | 1230 |  |  |  | AACCoreopsis |  |  |  | 0.43893
AAC | Cowslip | 2000 | 91/0 | 1.63 | 0.00865 | 0.00994 | 0.0107 | 0.0115 | 0.421 | 0.00865 | 1520 |  |  |  | AACCowslip |  |  |  | 0.42104
AAC | Lupine | 2500 | 91/0 | 1.823 | 0.00699 | 0.00845 | 0.00907 | 0.0097 | 0.404 | 0.00699 | 1700 |  |  |  | AACLupine |  |  |  | 0.40352
AAAC | 1439_2 | 1439.2 | 61/0 | 1.382 | 0.014 | 0.014669 | 0.015916 | 0.017167 | 0 | 0 | 897 |  |  |  | AAAC1439_2 |  | AAAC Ampacity APAR Catalog |  | 0.44688
AAAC | 1348_8 | 1348.8 | 61/0 | 1.338 | 0.01494 | 0.015654 | 0.016985 | 0.018319 | 0 | 0 | 865 |  |  |  | AAAC1348_8 |  |  |  | 0.45195
AAAC | 1259_6 | 1259.6 | 61/0 | 1.293 | 0.016 | 0.016765 | 0.01819 | 0.019619 | 0 | 0 | 831 |  |  |  | AAAC1259_6 |  |  |  | 0.4573
AAAC | 1165_1 | 1165.1 | 61/0 | 1.245 | 0.0173 | 0.018127 | 0.019668 | 0.021213 | 0 | 0 | 794 |  |  |  | AAAC1165_1 |  |  |  | 0.46322
AAAC | 1077_4 | 1077.4 | 61/0 | 1.196 | 0.0187 | 0.019594 | 0.021259 | 0.02293 | 0 | 0 | 760 |  |  |  | AAAC1077_4 |  |  |  | 0.46951
AAAC | Greeley | 927.2 | 37/0 | 1.108 | 0.02173 | 0.022769 | 0.024704 | 0.026645 | 0.678 | 0.107 | 694 |  |  |  | AAACGreeley |  | L,C and d_inch from Cmewire catalog |  | 0.48148
AAAC | Flint | 740.8 | 37/0 | 0.991 | 0.0272 | 0.028501 | 0.030923 | 0.033352 | 0.715 | 0.112 | 607 |  |  |  | AAACFlint |  | R from ASTM (dc) +3% |  | 0.49895
AAAC | Elgin | 652.4 | 19/0 | 0.927 | 0.3089 | 0.32367 | 0.35118 | 0.37877 | 0.751 | 0.118 | 564 |  |  |  | AAACElgin |  |  |  | 0.5094
AAAC | Darien | 559.5 | 19/0 | 0.858 | 0.03602 | 0.037742 | 0.04095 | 0.044167 | 0.522 | 0.0829 | 514 |  |  |  | AAACDarien |  |  |  | 0.52151
AAAC | Cairo | 465.4 | 19/0 | 0.783 | 0.0433 | 0.04537 | 0.049226 | 0.053094 | 0.536 | 0.0851 | 461 |  |  |  | AAACCairo |  |  |  | 0.53583
AAAC | Canton | 394.5 | 19/0 | 0.721 | 0.05107 | 0.053512 | 0.05806 | 0.062622 | 0.549 | 0.087 | 417 |  |  |  | AAACCanton |  |  |  | 0.54874
AAAC | Butte | 312.8 | 19/0 | 0.642 | 0.06443 | 0.067511 | 0.073248 | 0.079003 | 0.567 | 0.0896 | 362 |  |  |  | AAACButte |  |  |  | 0.56691
ACAR | Pelican | 503.6 | 15/4 | 0.814 | 0.0354 | 0.0364 | 0.03985 | 0.0433 | 0.531 | 0.0841 |  |  |  |  | ACARPelican |  |  |  | 0.52975
ACAR | Osprey | 587.2 | 15/4 | 0.879 | 0.0303 | 0.0312 | 0.03415 | 0.0371 | 0.518 | 0.0824 |  |  |  |  | ACAROsprey |  |  |  | 0.51772
ACAR | Dove | 649.5 | 18/19 | 0.927 | 0.0287 | 0.0295 | 0.0322 | 0.0349 | 0.509 | 0.0812 |  |  |  |  | ACARDove |  |  |  | 0.5094
ACAR | Dove | 653.1 | 12/7 | 0.927 | 0.0279 | 0.0288 | 0.03145 | 0.0341 | 0.509 | 0.0811 | 760 |  |  |  | ACARDove |  |  |  | 0.5094
ACAR | Grosbeak | 739.8 | 18/19 | 0.99 | 0.0252 | 0.0259 | 0.0283 | 0.0307 | 0.499 | 0.0793 | 814 |  |  |  | ACARGrosbeak |  |  |  | 0.4991
ACAR | Tern | 853.7 | 30/7 | 1.063 | 0.0208 | 0.0216 | 0.02365 | 0.0257 | 0.488 | 0.0777 | 907 |  |  |  | ACARTern |  |  |  | 0.48797
ACAR | Tern | 853.7 | 24/13 | 1.063 | 0.0213 | 0.0222 | 0.0242 | 0.0262 | 0.488 | 0.0777 |  |  |  |  | ACARTern |  |  |  | 0.48797
ACAR | Drake | 927.2 | 24/13 | 1.108 | 0.0208 | 0.0216 | 0.0234 | 0.0252 | 0.482 | 0.0767 |  |  |  |  | ACARDrake |  |  |  | 0.48148
ACAR | Rail | 1024.5 | 30/7 | 1.165 | 0.0173 | 0.0182 | 0.01985 | 0.0215 | 0.474 | 0.0756 | 1015 |  |  |  | ACARRail |  |  |  | 0.47362
ACAR | Rail | 1024.5 | 24/13 | 1.165 | 0.0178 | 0.0186 | 0.02025 | 0.0219 | 0.474 | 0.0756 |  |  |  |  | ACARRail |  | ACAR Ampacity from southwire catalog |  | 0.47362
ACAR | Cardinal | 1080.6 | 24/13 | 1.196 | 0.0168 | 0.0176 | 0.0192 | 0.0208 | 0.47 | 0.075 |  |  |  |  | ACARCardinal |  |  |  | 0.46951
ACAR | Cardinal | 1080.6 | 18/19 | 1.196 | 0.0172 | 0.0181 | 0.0197 | 0.0213 | 0.47 | 0.075 | 1028 |  |  |  | ACARCardinal |  |  |  | 0.46951
ACAR | Ortolan | 1109 | 30/7 | 1.212 | 0.016 | 0.0169 | 0.0184 | 0.0199 | 0.468 | 0.0747 | 1065 |  |  |  | ACAROrtolan |  |  |  | 0.46743
ACAR | Ortolan | 1109 | 24/13 | 1.212 | 0.0164 | 0.0172 | 0.01875 | 0.0203 | 0.468 | 0.0747 |  |  |  |  | ACAROrtolan |  |  |  | 0.46743
ACAR | Curlew | 1172 | 30/7 | 1.246 | 0.0152 | 0.016 | 0.01745 | 0.0189 | 0.463 | 0.074 | 1101 |  |  |  | ACARCurlew |  |  |  | 0.4631
ACAR | Curlew | 1172 | 18/19 | 1.246 | 0.0159 | 0.0166 | 0.01805 | 0.0195 | 0.463 | 0.074 |  |  |  |  | ACARCurlew |  |  |  | 0.4631
ACAR | Bluejay | 1198 | 30/7 | 1.259 | 0.0148 | 0.0155 | 0.01695 | 0.0184 | 0.462 | 0.0738 | 1115 |  |  |  | ACARBluejay |  |  |  | 0.46147
ACAR | Bluejay | 1198 | 24/13 | 1.259 | 0.0152 | 0.0159 | 0.01735 | 0.0188 | 0.462 | 0.0738 |  |  |  |  | ACARBluejay |  |  |  | 0.46147
ACAR | Bunting | 1277 | 54/7 | 1.302 | 0.0138 | 0.0149 | 0.01615 | 0.0174 | 0.456 | 0.0729 |  |  |  |  | ACARBunting |  |  |  | 0.45622
ACAR | Bunting | 1277 | 42/19 | 1.302 | 0.0142 | 0.0152 | 0.0165 | 0.0178 | 0.456 | 0.0729 |  |  |  |  | ACARBunting |  |  |  | 0.45622
ACAR | Bittern | 1361.5 | 54/7 | 1.345 | 0.0129 | 0.0138 | 0.01505 | 0.0163 | 0.451 | 0.0721 |  |  |  |  | ACARBittern |  |  |  | 0.45113
ACAR | Bobolink | 1534.4 | 42/19 | 1.427 | 0.0118 | 0.0127 | 0.01395 | 0.0152 | 0.442 | 0.0708 | 1314 |  |  |  | ACARBobolink |  |  |  | 0.44186
ACAR | Lapwing | 1703 | 48/13 | 1.504 | 0.0105 | 0.0115 | 0.0125 | 0.0135 | 0.434 | 0.0696 |  |  |  |  | ACARLapwing |  |  |  | 0.43364
ACAR | Falcon | 1798 | 42/19 | 1.545 | 0.0101 | 0.011 | 0.0119 | 0.0128 | 0.43 | 0.069 |  |  |  |  | ACARFalcon |  |  |  | 0.42943
ACAR | Chukar | 1933 | 42/19 | 1.602 | 0.0094 | 0.0102 | 0.0112 | 0.0122 | 0.424 | 0.0682 | 1465 |  |  |  | ACARChukar |  |  |  | 0.42376
ACAR | Bluebird | 2338 | 42/19 | 1.762 | 0.0078 | 0.0089 | 0.0096 | 0.0103 | 0.409 | 0.066 |  |  |  |  | ACARBluebird |  |  |  | 0.40885
ACAR | Bluebird | 2338 | 48/13 | 1.762 | 0.0077 | 0.0088 | 0.0095 | 0.0102 | 0.409 | 0.066 |  |  |  |  | ACARBluebird |  |  |  | 0.40885
ACAR | Kingfisher | 2493 | 54/37 | 1.821 | 0.0074 | 0.0087 | 0.00935 | 0.01 | 0.404 | 0.0652 | 1670 |  |  |  | ACARKingfisher |  |  |  | 0.4037
ACCC | OCEANSIDE | 383.2 | 26/0 | 0.68 | 0.04392 | 0.044962 | 0 | 0 | 0.5581 | 0.086591 | 558 |  |  |  | ACCCOCEANSIDE |  |  |  | 0.55791
ACCC | LINNET | 430.5 | 26/1 | 0.72 | 0.03892 | 0.03983 | 0 | 0 | 0.54912 | 0.085341 | 602 |  |  |  | ACCCLINNET |  |  |  | 0.54896
ACCC | ORIOLE | 438.6 | 26/2 | 0.741 | 0.038239 | 0.03911 | 0 | 0 | 0.5449 | 0.084413 | 612 |  |  |  | ACCCORIOLE |  |  |  | 0.54446
ACCC | WACO | 454 | 26/3 | 0.77 | 0.036951 | 0.037803 | 0 | 0 | 0.53856 | 0.083428 | 628 |  |  |  | ACCCWACO |  |  |  | 0.53845
ACCC | LAREDO | 529.8 | 26/4 | 0.807 | 0.031648 | 0.032424 | 0 | 0 | 0.53117 | 0.08267 | 687 |  |  |  | ACCCLAREDO |  |  |  | 0.5311
ACCC | IRVING | 609.5 | 26/5 | 0.882 | 0.027538 | 0.028239 | 0 | 0 | 0.51744 | 0.08036 | 753 |  |  |  | ACCCIRVING |  |  |  | 0.51719
ACCC | HAWK | 611.3 | 26/6 | 0.858 | 0.027424 | 0.028125 | 0 | 0 | 0.52166 | 0.081364 | 753 |  |  |  | ACCCHAWK |  |  |  | 0.52151
ACCC | DOVE | 713.5 | 26/7 | 0.927 | 0.023485 | 0.024129 | 0 | 0 | 0.50952 | 0.079545 | 826 |  |  |  | ACCCDOVE |  |  |  | 0.5094
ACCC | AMARILLO | 784.7 | 26/8 | 0.99 | 0.021439 | 0.022121 | 0 | 0 | 0.49949 | 0.077784 | 879 |  |  |  | ACCCAMARILLO |  |  |  | 0.4991
ACCC | GROSBEAK | 821.4 | 26/9 | 0.99 | 0.020473 | 0.021098 | 0 | 0 | 0.49949 | 0.078049 | 898 |  |  |  | ACCCGROSBEAK |  |  |  | 0.4991
ACCC | LUBBOCK | 903.9 | 26/10 | 1.04 | 0.018542 | 0.019148 | 0 | 0 | 0.49157 | 0.076913 | 956 |  |  |  | ACCCLUBBOCK |  |  |  | 0.49139
ACCC | GALVESTON | 1011.3 | 26/11 | 1.09 | 0.016572 | 0.017178 | 0 | 0 | 0.48418 | 0.07589 | 1022 |  |  |  | ACCCGALVESTON |  |  |  | 0.48404
ACCC | DRAKE | 1025.6 | 26/12 | 1.108 | 0.016345 | 0.016894 | 0 | 0 | 0.48154 | 0.075398 | 1036 |  |  |  | ACCCDRAKE |  |  |  | 0.48148
ACCC | CURLEW | 1033 | 26/13 | 1.14 | 0.016326 | 0.017008 | 0 | 0 | 0.47731 | 0.074621 | 1042 |  |  |  | ACCCCURLEW |  |  |  | 0.47702
ACCC | PLANO | 1059.5 | 26/14 | 1.127 | 0.015909 | 0.016591 | 0 | 0 | 0.4789 | 0.075208 | 1050 |  |  |  | ACCCPLANO |  |  |  | 0.47881
ACCC | CORPUS_CHRISTI | 1103 | 26/15 | 1.146 | 0.015265 | 0.015966 | 0 | 0 | 0.47626 | 0.074848 | 1076 |  |  |  | ACCCCORPUS_CHRISTI |  |  |  | 0.4762
ACCC | ARLINGTON | 1151 | 26/16 | 1.177 | 0.01464 | 0.015322 | 0 | 0 | 0.47203 | 0.074148 | 1106 |  |  |  | ACCCARLINGTON |  |  |  | 0.47202
ACCC | CARDINAL | 1221.8 | 26/17 | 1.198 | 0.013788 | 0.014432 | 0 | 0 | 0.46939 | 0.073864 | 1146 |  |  |  | ACCCCARDINAL |  |  |  | 0.46925
ACCC | FORT_WORTH | 1300.4 | 26/18 | 1.24 | 0.012955 | 0.013655 | 0 | 0 | 0.46411 | 0.073011 | 1189 |  |  |  | ACCCFORT_WORTH |  |  |  | 0.46385
ACCC | EL_PASO | 1349.9 | 26/19 | 1.252 | 0.012481 | 0.01322 | 0 | 0 | 0.46253 | 0.072917 | 1212 |  |  |  | ACCCEL_PASO |  |  |  | 0.46235
ACCC | BEAUMONT | 1428.6 | 26/20 | 1.294 | 0.011799 | 0.012519 | 0 | 0 | 0.45725 | 0.072102 | 1257 |  |  |  | ACCCBEAUMONT |  |  |  | 0.45718
ACCC | SAN_ANTONIO | 1474.9 | 26/21 | 1.315 | 0.01142 | 0.011799 | 0 | 0 | 0.45461 | 0.071723 | 1302 |  |  |  | ACCCSAN_ANTONIO |  |  |  | 0.45466
ACCC | BITTERN | 1581.6 | 26/22 | 1.345 | 0.01072 | 0.01142 | 0 | 0 | 0.45144 | 0.071364 | 1331 |  |  |  | ACCCBITTERN |  |  |  | 0.45113
ACCC | DALLAS | 1794.9 | 26/23 | 1.452 | 0.0094129 | 0.010341 | 0 | 0 | 0.4393 | 0.069545 | 1434 |  |  |  | ACCCDALLAS |  |  |  | 0.43915
ACCC | HOUSTON | 1927.4 | 26/24 | 1.506 | 0.0086932 | 0.0096591 | 0 | 0 | 0.43349 | 0.068655 | 1502 |  |  |  | ACCCHOUSTON |  |  |  | 0.43343
ACCC | LAPWING | 1948.9 | 26/25 | 1.504 | 0.0086742 | 0.0096023 | 0 | 0 | 0.43402 | 0.068807 | 1502 |  |  |  | ACCCLAPWING |  |  |  | 0.43364
ACCC | FALCON | 2045.1 | 26/26 | 1.545 | 0.0082576 | 0.009072 | 0 | 0 | 0.42979 | 0.068125 | 1555 |  |  |  | ACCCFALCON |  |  |  | 0.42943
ACCC | BLUEBIRD | 2740.6 | 26/27 | 1.762 | 0.0061742 | 0.0073295 | 0 | 0 | 0.4092 | 0.065246 | 1808 |  |  |  | ACCCBLUEBIRD |  |  |  | 0.40885
ACSS | Partridge | 266.8 | 26/7 | 0.642 | 0.0619 | 0.0633 |  | 0.0762 | 0.565 | 0.088 |  | 366.9 | 9.7 | 11.4 | ACSSPartridge |  |  |  | 0.56691
ACSS | Oriole | 336.4 | 30/7 | 0.741 | 0.0488 | 0.0499 |  | 0.0601 | 0.544 | 0.084 |  | 526.4 | 16.3 | 19.1 | ACSSOriole |  |  |  | 0.54446
ACSS | Linnet | 336.4 | 26/7 | 0.72 | 0.0492 | 0.0503 |  | 0.0605 | 0.549 | 0.085 |  | 462 | 12.3 | 14.4 | ACSSLinnet |  |  |  | 0.54896
ACSS | Lark | 397.5 | 30/7 | 0.806 | 0.0413 | 0.0423 |  | 0.0509 | 0.533 | 0.082 |  | 621.8 | 19.3 | 22.6 | ACSSLark |  |  |  | 0.53129
ACSS | Ibis | 397.5 | 26/7 | 0.783 | 0.0416 | 0.0426 |  | 0.0512 | 0.539 | 0.084 |  | 546 | 14.2 | 16.5 | ACSSIbis |  |  |  | 0.53583
ACSS | Hen | 477 | 30/7 | 0.883 | 0.0344 | 0.0353 |  | 0.0424 | 0.517 | 0.08 |  | 746.4 | 22.7 | 26.7 | ACSSHen |  |  |  | 0.51701
ACSS | Hawk | 477 | 26/7 | 0.858 | 0.0347 | 0.0355 |  | 0.0427 | 0.522 | 0.081 |  | 655.3 | 17.1 | 19.8 | ACSSHawk |  |  |  | 0.52151
ACSS | Flicker | 477 | 24/7 | 0.846 | 0.0348 | 0.0357 |  | 0.0429 | 0.524 | 0.082 |  | 613.9 | 14.2 | 16.4 | ACSSFlicker |  |  |  | 0.52371
ACSS | Eagle | 556.5 | 30/7 | 0.953 | 0.0295 | 0.0303 |  | 0.0364 | 0.505 | 0.079 |  | 870.7 | 26.5 | 31.1 | ACSSEagle |  |  |  | 0.50507
ACSS | Dove | 556.5 | 26/7 | 0.927 | 0.0297 | 0.0305 |  | 0.0367 | 0.51 | 0.08 |  | 765.2 | 19.9 | 23.1 | ACSSDove |  |  |  | 0.5094
ACSS | Parakeet | 556.5 | 24/7 | 0.914 | 0.0298 | 0.0307 |  | 0.0368 | 0.512 | 0.08 |  | 716.1 | 16.6 | 19.1 | ACSSParakeet |  |  |  | 0.51161
ACSS | Peacock | 605 | 24/7 | 0.953 | 0.0274 | 0.0282 |  | 0.0339 | 0.505 | 0.079 |  | 778.8 | 18.1 | 20.8 | ACSSPeacock |  |  |  | 0.50507
ACSS | Egret | 636 | 30/19 | 1.019 | 0.0258 | 0.0266 |  | 0.0319 | 0.495 | 0.077 |  | 987.2 | 30.9 | 36.6 | ACSSEgret |  |  |  | 0.49458
ACSS | Grosbeak | 636 | 26/7 | 0.99 | 0.026 | 0.0268 |  | 0.0321 | 0.5 | 0.078 |  | 874.2 | 22.4 | 26 | ACSSGrosbeak |  |  |  | 0.4991
ACSS | Rook | 636 | 24/7 | 0.977 | 0.0261 | 0.0269 |  | 0.0323 | 0.502 | 0.079 |  | 818.2 | 19 | 21.9 | ACSSRook |  |  |  | 0.50117
ACSS | Flamingo | 666.6 | 24/7 | 1 | 0.0249 | 0.0257 |  | 0.0308 | 0.498 | 0.078 |  | 857.9 | 19.9 | 22.9 | ACSSFlamingo |  |  |  | 0.49753
ACSS | Redwing | 715.5 | 30/19 | 1.081 | 0.023 | 0.0237 |  | 0.0284 | 0.486 | 0.076 |  | 1109 | 34 | 39.8 | ACSSRedwing |  |  |  | 0.48534
ACSS | Starling | 715.5 | 26/7 | 1.051 | 0.0231 | 0.0238 |  | 0.0286 | 0.49 | 0.077 |  | 983.7 | 25.2 | 29.3 | ACSSStarling |  |  |  | 0.48974
ACSS | Mallard | 795 | 30/19 | 1.14 | 0.0207 | 0.0213 |  | 0.0256 | 0.477 | 0.074 |  | 1234 | 37.9 | 44.3 | ACSSMallard |  |  |  | 0.47702
ACSS | Condor | 795 | 54/7 | 1.092 | 0.0209 | 0.0216 |  | 0.0267 | 0.484 | 0.076 |  | 1022 | 23.3 | 26.9 | ACSSCondor |  |  |  | 0.48375
ACSS | Tern | 795 | 45/7 | 1.063 | 0.021 | 0.0218 |  | 0.0263 | 0.488 | 0.076 |  | 895 | 15.2 | 17.4 | ACSSTern |  |  |  | 0.48797
ACSS | Drake | 795 | 26/7 | 1.108 | 0.0208 | 0.0215 |  | 0.0258 | 0.482 | 0.076 |  | 1093 | 28 | 32.6 | ACSSDrake |  |  |  | 0.48148
ACSS | Cuckoo | 795 | 24/7 | 1.092 | 0.0209 | 0.0216 |  | 0.0259 | 0.484 | 0.076 |  | 1023 | 23.3 | 26.9 | ACSSCuckoo |  |  |  | 0.48375
ACSS | Canary | 900 | 54/7 | 1.162 | 0.0184 | 0.0192 |  | 0.0236 | 0.474 | 0.074 |  | 1158 | 26.4 | 30.5 | ACSSCanary |  |  |  | 0.47403
ACSS | Ruddy | 900 | 45/7 | 1.131 | 0.0186 | 0.0194 |  | 0.0233 | 0.479 | 0.076 |  | 1013 | 17 | 19.2 | ACSSRuddy |  |  |  | 0.47826
ACSS | Cardinal | 954 | 54/7 | 1.196 | 0.0174 | 0.0181 |  | 0.0223 | 0.47 | 0.076 |  | 1227 | 28 | 32.3 | ACSSCardinal |  |  |  | 0.46951
ACSS | Rail | 954 | 45/7 | 1.165 | 0.0175 | 0.0183 |  | 0.0221 | 0.474 | 0.075 |  | 1074 | 18 | 20.4 | ACSSRail |  |  |  | 0.47362
ACSS | Curlew | 1033.5 | 54/7 | 1.245 | 0.0161 | 0.0168 |  | 0.0206 | 0.464 | 0.073 |  | 1329 | 30.3 | 35 | ACSSCurlew |  |  |  | 0.46322
ACSS | Ortolan | 1033.5 | 45/7 | 1.212 | 0.0162 | 0.017 |  | 0.0204 | 0.468 | 0.074 |  | 1163 | 19.5 | 22 | ACSSOrtolan |  |  |  | 0.46743
ACSS | Finch | 1113 | 54/19 | 1.293 | 0.015 | 0.0157 |  | 0.0193 | 0.458 | 0.07 |  | 1430 | 33.2 | 38.7 | ACSSFinch |  |  |  | 0.4573
ACSS | Bluejay | 1113 | 45/7 | 1.259 | 0.015 | 0.0159 |  | 0.019 | 0.462 | 0.073 |  | 1254 | 21.1 | 23.8 | ACSSBluejay |  |  |  | 0.46147
ACSS | Grackle | 1192.5 | 54/19 | 1.338 | 0.014 | 0.0147 |  | 0.018 | 0.452 | 0.071 |  | 1531 | 35.5 | 41.5 | ACSSGrackle |  |  |  | 0.45195
ACSS | Bunting | 1192.5 | 45/7 | 1.302 | 0.014 | 0.0149 |  | 0.0178 | 0.456 | 0.072 |  | 1342 | 23.5 | 25.4 | ACSSBunting |  |  |  | 0.45622
ACSS | Pheasant | 1272 | 54/19 | 1.382 | 0.0131 | 0.0139 |  | 0.0169 | 0.447 | 0.07 |  | 1634 | 37.3 | 43 | ACSSPheasant |  |  |  | 0.44688
ACSS | Bittern | 1272 | 45/7 | 1.345 | 0.0132 | 0.014 |  | 0.0167 | 0.451 | 0.072 |  | 1432 | 24 | 27.1 | ACSSBittern |  |  |  | 0.45113
ACSS | Martin | 1351 | 54/19 | 1.424 | 0.012 | 0.013 |  | 0.016 | 0.442 | 0.07 |  | 1735 | 39.6 | 45.6 | ACSSMartin |  |  |  | 0.44219
ACSS | Dipper | 1351 | 45/7 | 1.386 | 0.0124 | 0.0132 |  | 0.0158 | 0.447 | 0.071 |  | 1521 | 25.5 | 28.8 | ACSSDipper |  |  |  | 0.44643
ACSS | Plover | 1431 | 54/19 | 1.465 | 0.012 | 0.012 |  | 0.015 | 0.438 | 0.069 |  | 1838 | 41.9 | 48.3 | ACSSPlover |  |  |  | 0.43775
ACSS | Bobolink | 1431 | 45/7 | 1.427 | 0.012 | 0.013 |  | 0.015 | 0.442 | 0.07 |  | 1611 | 27 | 30.5 | ACSSBobolink |  |  |  | 0.44186
ACSS | Falcon | 1590 | 54/19 | 1.545 | 0.011 | 0.011 |  | 0.014 | 0.43 | 0.068 |  | 2042 | 46.6 | 53.7 | ACSSFalcon |  |  |  | 0.42943
ACSS | Lapwing | 1590 | 45/7 | 1.504 | 0.011 | 0.012 |  | 0.014 | 0.434 | 0.069 |  | 1790 | 29.6 | 33.5 | ACSSLapwing |  |  |  | 0.43364
ACSS | Chukar* | 1780 | 84/19 | 1.602 | 0.009 | 0.01 |  | 0.012 | 0.424 | 0.067 |  | 2072 | 38.2 | 43.9 | ACSSChukar* |  |  |  | 0.42376
ACSS | Bluebird* | 2156 | 84/19 | 1.762 | 0.008 | 0.009 |  | 0.01 | 0.409 | 0.065 |  | 2508 | 45.5 | 51.7 | ACSSBluebird* |  |  |  | 0.40885
ACSS | Kiwi* | 2167 | 72/7 | 1.735 | 0.008 | 0.009 |  | 0.01 | 0.411 | 0.068 |  | 2301 | 30.8 | 34.1 | ACSSKiwi* |  |  |  | 0.41127
ACSS | Thrasher* | 2312 | 76/19 | 1.802 | 0.007 | 0.009 |  | 0.01 | 0.405 | 0.065 |  | 2523 | 38.1 | 43 | ACSSThrasher* |  |  |  | 0.40534

## G_wire
type | awg | size_kcmil | wire_diameter_inch | diameter_inch | breaking_load_lb | weight_lb_kft | R_20dc_ohm_kft | area_inches
Alumoweld | 37/5 | 1225 | 0.1819 | 1.27 | 142800 | 2802 | 0.0425 | 620.6
Alumoweld | 37/6 | 971.3 | 0.162 | 1.13 | 120200 | 2222 | 0.0536 | 492.2
Alumoweld | 37/7 | 770.3 | 0.1443 | 1.01 | 100700 | 1762 | 0.0675 | 390.3
Alumoweld | 37/8 | 610.9 | 0.1285 | 0.899 | 84200 | 1398 | 0.0852 | 309.5
Alumoweld | 37/9 | 484.4 | 0.1144 | 0.801 | 66700 | 1108 | 0.1074 | 245.5
Alumoweld | 37/10 | 384.2 | 0.1019 | 0.713 | 52950 | 879 | 0.1354 | 194.6
Alumoweld | 19/5 | 628.9 | 0.1819 | 0.91 | 73350 | 1430 | 0.0822 | 318.7
Alumoweld | 19/6 | 498.8 | 0.162 | 0.81 | 61700 | 1134 | 0.1037 | 252.7
Alumoweld | 19/7 | 395.5 | 0.1443 | 0.721 | 51730 | 889.5 | 0.1308 | 200.4
Alumoweld | 19/8 | 313.7 | 0.1285 | 0.642 | 43240 | 713.5 | 0.1649 | 159
Alumoweld | 19/9 | 248.8 | 0.1144 | 0.572 | 34290 | 565.8 | 0.2079 | 126.1
Alumoweld | 19/10 | 197.3 | 0.1019 | 0.509 | 27190 | 448.7 | 0.2622 | 99.93
Alumoweld | 7/5 | 231.7 | 0.1819 | 0.546 | 27030 | 524.9 | 0.2264 | 117.4
Alumoweld | 7/6 | 183.8 | 0.162 | 0.486 | 22730 | 416.3 | 0.2803 | 93.09
Alumoweld | 7/7 | 145.7 | 0.1443 | 0.433 | 19060 | 330 | 0.3535 | 73.87
Alumoweld | 7/8 | 115.6 | 0.1285 | 0.385 | 15930 | 261.8 | 0.4458 | 58.56
Alumoweld | 7/9 | 91.65 | 0.1144 | 0.343 | 12630 | 207.6 | 0.5621 | 46.44
Alumoweld | 7/10 | 72.68 | 0.1019 | 0.306 | 10020 | 164.7 | 0.7088 | 36.82
Alumoweld | 7/11 | 57.59 | 0.0907 | 0.272 | 7945 | 130.6 | 0.8938 | 29.18
Alumoweld | 7/12 | 45.71 | 0.0808 | 0.242 | 6301 | 103.6 | 1.127 | 23.16
Alumoweld | 3/5 | 99.31 | 0.1819 | 0.392 | 12230 | 224.5 | 0.5177 | 50.32
Alumoweld | 3/6 | 78.75 | 0.162 | 0.349 | 10280 | 178.1 | 0.6528 | 39.9
Alumoweld | 3/7 | 62.45 | 0.1443 | 0.311 | 8621 | 141.2 | 0.8232 | 31.64
Alumoweld | 3/8 | 49.53 | 0.1285 | 0.277 | 7206 | 112 | 1.038 | 25.1
Alumoweld | 3/9 | 39.28 | 0.1144 | 0.247 | 5715 | 88.81 | 1.309 | 19.9
Alumoweld | 3/10 | 31.15 | 0.1019 | 0.22 | 4532 | 70.43 | 1.651 | 15.78
ACSR | 4/0 6/1 | 484.4 | 0.1144 | 0.563 | 66700 | 1108 | 0.11212 | 245.5

## Validation
VALIDATIONS
Structure type | conductor_type
Lattice | AAC
Pole | ACSR
H Frame | AAAC
Y | ACAR

## Sources
Sources
Insulators string distance:IEC 60071-2 Insulation co-ordination application guite part 2 (creepage distance). AND IEC 60305 IEC Insulators classes
EPRI Transmission reference book
Stevenson, Grainger
| typical bundling | Oregon state U | Section 4 Transmission Lines.pdf (oregonstate.edu)

## TL_Geometry (2)
code | structure_type | company | state | n_circuits | n_ground_w | voltage_kv | Creep_Dist_mm_kv | Insul_Creep_Dist_mm | Insul_Spac_mm | L_Ins_String_ft | ha1t_ft | hb1t_ft | hc1t_ft | Sa1t_ft | Sb1t_ft | Sc1t_ft | hg11t_ft | Sg11t_ft | hg21t_ft | Sg21t_ft | ha2t_ft | hb2t_ft | hc2t_ft | Sa2t_ft | Sb2t_ft | Sc2t_ft | ha1 (ft) | ha1 (inch) | hb1 (ft) | hb1 (inch) | hc1 (ft) | hc1 (inch) | Sa1 (ft) | Sa1 (inch) | Sb1 (ft) | Sb1 (inch) | Sc1 (ft) | Sc1 (inch) | hg11 (ft) | hg11 (inch) | Sg11 (ft) | Sg11 (inch) | hg21 (ft) | hg21 (inch) | Sg21 (ft) | Sg21 (inch) | ha2 (ft) | ha2 (inch) | hb2 (ft) | hb2 (inch) | hc2 (ft) | hc2 (inch) | Sa2 (ft) | Sa2 (inch) | Sb2 (ft) | Sb2 (inch) | Sc2 (ft) | Sc2 (inch)
3L1 | Lattice | Iowa Public Service Co | Iowa | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -23.75 | 0 | 23.75 | 87.5 | -17.8125 | 87.5 | 17.8125 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -23 | -9 | 0 | 0 | 23 | 9 | 87 | 6 | -17.25 | -6.75 | 87 | 6 | 17.25 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L2 | Lattice | Indianapolis Power and Light Company, Western Power Area Administration | Indiana, Colorado | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -32 | 0 | 32 | 96.5 | -21.5 | 96.5 | 21.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -32 | 0 | 0 | 0 | 32 | 0 | 96 | 6 | -21 | -6 | 96 | 6 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L3 | Lattice | Consumers Power Company | Michigan | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 59.1594 | 59.1594 | -24.5 | 0 | 24.5 | 87.5 | -16.5 | 87.5 | 16.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | -24 | -6 | 0 | 0 | 24 | 6 | 87 | 6 | -16 | -6 | 87 | 6 | 16 | 6
3L4 | Lattice | Pennsylvania Electric Co | Pensylvania | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.1594 | 44.1594 | 44.1594 | -22.6667 | 0 | 22.6667 | 73 | -18.5833 | 73 | 18.5833 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 0 | 55 | 0 | 55 | 0 | -22 | -8 | 0 | 0 | 22 | 8 | 73 | 0 | -18 | -7 | 73 | 0 | 18 | 7
3L5 | Lattice | Northern Indiana Public Service | Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 79.1594 | 79.1594 | 79.1594 | -24 | 0 | 24 | 102 | -21.6 | 102 | 21.6 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 90 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 102 | 0 | -21.6 | 0 | 102 | 0 | 21.6 | 0
3L6 | Lattice | Cleveland electric iluminating | Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 43.6594 | 43.6594 | 43.6594 | -23 | 0 | 23 | 94.5 | -20.5 | 94.5 | 20.5 | 72.1594 | 72.1594 | 72.1594 | 23 | 0 | -23 | 54 | 6 | 54 | 6 | 54 | 6 | -23 | 0 | 0 | 0 | 23 | 0 | 93 | 18 | -20 | -6 | 93 | 18 | 20 | 6 | 82 | 12 | 82 | 12 | 82 | 12 | 23 | 0 | 0 | 0 | -23 | 0
3L7 | Lattice | Consolidated Edison Co | New York | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 41.826 | 64.826 | 87.826 | -19 | -17.5 | -15.3333 | 104.6667 | -12 | 104.6667 | 12 | 87.826 | 64.826 | 41.826 | 15.3333 | 17.5 | 19 | 52 | 8 | 75 | 8 | 98 | 8 | -19 | 0 | -17 | -6 | -15 | -4 | 104 | 8 | -12 | 0 | 104 | 8 | 12 | 0 | 98 | 8 | 75 | 8 | 52 | 8 | 15 | 4 | 17 | 6 | 19 | 0
3L8 | Lattice | Oklahoma Gas & Electric Co, American Electric Power Co | Oklahoma, Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 93.1594 | 117.1594 | -22 | -37 | -22 | 142 | -11 | 142 | 11 | 117.1594 | 93.1594 | 69.1594 | 22 | 37 | 22 | 80 | 0 | 104 | 0 | 128 | 0 | -22 | 0 | -37 | 0 | -22 | 0 | 142 | 0 | -11 | 0 | 142 | 0 | 11 | 0 | 128 | 0 | 104 | 0 | 80 | 0 | 22 | 0 | 37 | 0 | 22 | 0
3L9 | Lattice | Consumers Power Company, Indianapolis Power and Light Company | Michigan, Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 89.1594 | 111.1594 | -18 | -29 | -17 | 137 | -24 | 137 | 24 | 111.1594 | 89.1594 | 69.1594 | 17 | 29 | 18 | 80 | 0 | 100 | 0 | 122 | 0 | -18 | 0 | -29 | 0 | -17 | 0 | 137 | 0 | -24 | 0 | 137 | 0 | 24 | 0 | 122 | 0 | 100 | 0 | 80 | 0 | 17 | 0 | 29 | 0 | 18 | 0
3L10 | Lattice | Detroit Edison | Michigan | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 53.1594 | 74.6594 | 98.6594 | -20.5 | -27 | -18.5 | 119.5 | -25.75 | 119.5 | 25.75 | 98.6594 | 74.6594 | 53.1594 | 18.5 | 27 | 20.5 | 64 | 0 | 85 | 6 | 109 | 6 | -20 | -6 | -27 | 0 | -18 | -6 | 119 | 6 | -25 | -9 | 119 | 6 | 25 | 9 | 109 | 6 | 85 | 6 | 64 | 0 | 18 | 6 | 27 | 0 | 20 | 6
3L13 | Lattice | Union electric company | Missouri, Nebraska, Minnesota | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 91.1594 | 65.1594 | 65.1594 | -17.6667 | -37 | -17 | 109 | -23.3333 | 109 | 23.3333 | 91.1594 | 65.1594 | 65.1594 | 17.6667 | 17 | 37 | 102 | 0 | 76 | 0 | 76 | 0 | -17 | -8 | -37 | 0 | -17 | 0 | 109 | 0 | -23 | -4 | 109 | 0 | 23 | 4 | 102 | 0 | 76 | 0 | 76 | 0 | 17 | 8 | 17 | 0 | 37 | 0
3L14 | Lattice | Texas electric service & Light Co | Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 77.1594 | 52.1594 | 52.1594 | -25.5833 | -37.8333 | -14.3333 | 103 | -15.6667 | 103 | 15.6667 | 77.1594 | 52.1594 | 52.1594 | 25.5833 | 14.3333 | 37.8333 | 88 | 0 | 63 | 0 | 63 | 0 | -25 | -7 | -37 | -10 | -14 | -4 | 103 | 0 | -15 | -8 | 103 | 0 | 15 | 8 | 88 | 0 | 63 | 0 | 63 | 0 | 25 | 7 | 14 | 4 | 37 | 10
3L15 | Lattice | Commonwealth Edison Company | Chicago | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 97.1594 | 54.1594 | 54.1594 | -28.5 | -40.5 | -16.5 | 117 | -40.5 | 117 | 40.5 | 97.1594 | 54.1594 | 54.1594 | 69 | 16.5 | 81 | 108 | 0 | 65 | 0 | 65 | 0 | -28.5 | 0 | -40.5 | 0 | -16.5 | 0 | 117 | 0 | -40.5 | 0 | 117 | 0 | 40.5 | 0 | 108 | 0 | 65 | 0 | 65 | 0 | 69 | 0 | 16.5 | 0 | 81 | 0
3P1 | Pole | Dayton Power & Light company | Ohio | 1 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 64.1594 | 75.6594 | 87.1594 | 9 | -9 | 9 | 131.5 | 0 | 0 | 0 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 75 | 0 | 86 | 6 | 98 | 0 | 9 | 0 | -9 | 0 | 9 | 0 | 131 | 6 | 0 | 0 | 0 | 0 | 0 | 0
3P2 | Pole | Cleveland electric iluminating, Indianapolis Power and Light Company, Northeast Utilities | Ohio, Indiana, New Hampshire, Massachusets, Connecticut | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 54.1594 | 77.1594 | 100.1594 | -15 | -15 | -15 | 132 | -14 | 132 | 14 | 100.1594 | 77.1594 | 54.1594 | 15 | 15 | 15 | 65 | 0 | 88 | 0 | 111 | 0 | -15 | 0 | -15 | 0 | -15 | 0 | 132 | 0 | -14 | 0 | 132 | 0 | 14 | 0 | 111 | 0 | 88 | 0 | 65 | 0 | 15 | 0 | 15 | 0 | 15 | 0
3P3 | Pole | Northern States Power Company, Wisconsin Electric Power Co | Minnesota, Wisconsin | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 90.1594 | 115.1594 | -14.25 | -21.25 | -14.25 | 135 | -17 | 135 | 17 | 115.1594 | 90.1594 | 65.1594 | 14.25 | 21.25 | 14.25 | 76 | 0 | 101 | 0 | 126 | 0 | -14 | -3 | -21 | -3 | -14 | -3 | 135 | 0 | -17 | 0 | 135 | 0 | 17 | 0 | 126 | 0 | 101 | 0 | 76 | 0 | 14 | 3 | 21 | 3 | 14 | 3
3P4 | Pole | Consolidated Edison Co, Houston Lightning Company, SouthWestern electric company | New York, Texas, Arkansas, Lousiana, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 81.1594 | 97.1594 | -11 | -11 | -11 | 111.5 | -8 | 111.5 | 8 | 97.1594 | 81.1594 | 65.1594 | 11 | 11 | 11 | 76 | 0 | 92 | 0 | 108 | 0 | -11 | 0 | -11 | 0 | -11 | 0 | 111 | 6 | -8 | 0 | 111 | 6 | 8 | 0 | 108 | 0 | 92 | 0 | 76 | 0 | 11 | 0 | 11 | 0 | 11 | 0
3P5 | Pole | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 72 | 97 | 122 | -11 | -19 | -11 | 140 | -7 | 140 | 7 | 122 | 97 | 72 | 11 | 19 | 11 | 82.8406 | 0 | 107.8406 | 0 | 132.8406 | 0 | -11 | 0 | -19 | 0 | -11 | 0 | 140 | 0 | -7 | 0 | 140 | 0 | 7 | 0 | 132.8406 | 0 | 107.8406 | 0 | 82.8406 | 0 | 11 | 0 | 19 | 0 | 11 | 0
3P6 | Pole | Dayton Power & Light company | Ohio | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 81.6594 | 104.1594 | -9 | -13 | -9 | 145.5 | 0 | 0 | 0 | 104.1594 | 81.6594 | 59.1594 | -9 | -13 | -9 | 70 | 0 | 92 | 6 | 114 | 12 | -9 | 0 | -13 | 0 | -9 | 0 | 144 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 12 | 92 | 6 | 70 | 0 | -9 | 0 | -13 | 0 | -9 | 0
3P7 | Pole | Illinois Power Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.826 | 80.826 | 80.826 | -15.5 | -41 | -16 | 127.6667 | -30 | 127.6667 | 30 | 116.826 | 80.826 | 80.826 | 15.5 | 16 | 41 | 127 | 8 | 91 | 8 | 91 | 8 | -15 | -6 | -41 | 0 | -16 | 0 | 127 | 8 | -30 | 0 | 127 | 8 | 30 | 0 | 127 | 8 | 91 | 8 | 91 | 8 | 15 | 6 | 16 | 0 | 41 | 0
3P8 | Pole | Commonwealth Edison Company | Chicago | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 98.1594 | 55.1594 | 55.1594 | -22 | -33 | -10 | 118 | 0 | 0 | 0 | 98.1594 | 55.1594 | 55.1594 | 22 | 10 | 33 | 109 | 0 | 66 | 0 | 66 | 0 | -22 | 0 | -33 | 0 | -10 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 66 | 0 | 66 | 0 | 22 | 0 | 10 | 0 | 33 | 0
3H1 | H frame | Public Service Company of New Hampshire | New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -18 | 0 | 18 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -18 | 0 | 0 | 0 | 18 | 0 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H2 | H frame | Utah Power and Light Company | Utah | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 62.1594 | 62.1594 | 62.1594 | -27 | 0 | 27 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 73 | 0 | 73 | 0 | 73 | 0 | -26 | -12 | 0 | 0 | 26 | 12 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H3 | H frame | Niagara Mohawk Power Corporation, Illinois Power Company, Central Maine Power Co | New York, Illinois, Maine, New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.826 | 44.826 | 44.826 | -26 | 0 | 26 | 65.5 | -13 | 65.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 8 | 55 | 8 | 55 | 8 | -26 | 0 | 0 | 0 | 26 | 0 | 64 | 18 | -13 | 0 | 64 | 18 | 13 | 0
3H4 | H frame | Public Service Company of New Hampshire, Northeast Utilities, New York State Electric & Gas, Vermont Electric Company, Wisconsin Public Service Corp | New Hampshire, Massachusets, Connecticut, New York, Vermont, Wisconsin | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 50.1594 | 50.1594 | 50.1594 | -26 | 0 | 26 | 73.5 | -13 | 73.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 61 | 0 | 61 | 0 | 61 | 0 | -26 | 0 | 0 | 0 | 26 | 0 | 73.5 | 0 | -13 | 0 | 73.5 | 0 | 13 | 0
3H5 | H frame | El paso electric company | Texas, New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 59.1594 | 52.6594 | -27 | 0 | 27 | 78 | -13.5 | 78 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 69 | 12 | 63 | 6 | -26 | -12 | 0 | 0 | 26 | 12 | 77 | 12 | -13.5 | 0 | 77 | 12 | 13.5 | 0
3H6 | H frame | Northern States Power Company, Wisconsin Electric Power Co, Kansas Gas & Electric Co | Minnesota, Wisconsin, Kansas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 46.6594 | 58.1594 | 46.6594 | -28.25 | 0 | 28.25 | 69 | -15.25 | 69 | 15.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 57 | 6 | 68 | 12 | 57 | 6 | -28 | -3 | 0 | 0 | 28 | 3 | 68 | 12 | -15 | -3 | 68 | 12 | 15 | 3
3H7 | H frame | Public Service Company of New Mexico | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -23.5 | 0 | 23.5 | 68.5 | -13.5 | 68.5 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -23 | -6 | 0 | 0 | 23 | 6 | 68 | 6 | -13.5 | 0 | 68 | 6 | 13.5 | 0
3H8 | H frame | Union electric company | Missouri, Nebraska, Minnesota | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 51.1594 | 51.1594 | 51.1594 | -24 | 0 | 24 | 72.5 | -26 | 72.5 | 26 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 62 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 72 | 6 | -26 | 0 | 72 | 6 | 26 | 0
3H9 | H frame | New Englad Electric System | New Englad, New Hampshire, Massachusets | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 52.6594 | 52.6594 | -20 | 0 | 20 | 74.5 | -9.5 | 74.5 | 9.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 63 | 6 | 63 | 6 | -19 | -12 | 0 | 0 | 19 | 12 | 74 | 6 | -9 | -6 | 74 | 6 | 9 | 6
3H10 | H frame | Boston Edison Company | Massachusets | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 96 | 70 | 70 | -10 | -32.75 | -10 | 111 | -27.25 | 111 | 27.25 | 96 | 70 | 70 | 10 | 10 | 32.75 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | -10 | 0 | -32 | -9 | -10 | 0 | 111 | 0 | -27 | -3 | 111 | 0 | 27 | 3 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | 10 | 0 | 10 | 0 | 32 | 9
3Y1 | Y | Tucson Gas & Electric Co | Arizona | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 109.2427 | 84.6594 | 84.6594 | 0 | -15 | 15 | 120.0833 | -13.5 | 120.0833 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 119 | 13 | 95 | 6 | 95 | 6 | 0 | 0 | -15 | 0 | 15 | 0 | 119 | 13 | -13.5 | 0 | 119 | 13 | 13.5 | 0
3Y2 | Y | Pacific Power Light corp |  | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -13.5 | 13.5 | 127 | -10 | 127 | 10 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -13 | -6 | 13 | 6 | 127 | 0 | -10 | 0 | 127 | 0 | 10 | 0
3Y3 | Y | SouthWestern electric company | Arkansas, Lousiana, Texas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -19.8333 | 19.8333 | 127 | -9 | 127 | 9 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -19.5 | -4 | 19.5 | 4 | 127 | 0 | -9 | 0 | 127 | 0 | 9 | 0
5L1 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 96.7889 | 69.2889 | 69.2889 | 0 | -20 | 20 | 122.25 | -13 | 122.25 | 13 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 112 | 6 | 85 | 0 | 85 | 0 | 0 | 0 | -20 | 0 | 20 | 0 | 121 | 15 | -13 | 0 | 121 | 15 | 13 | 0
5L2 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 98.2889 | 69.2889 | 69.2889 | 0 | -15.3333 | 15.3333 | 121 | -12 | 121 | 12 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 114 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -15 | -4 | 15 | 4 | 121 | 0 | -12 | 0 | 121 | 0 | 12 | 0
5L3 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 90.2889 | 74.2889 | 74.2889 | 0 | -29 | 29 | 106 | -15 | 106 | 15 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 106 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | -29 | 0 | 29 | 0 | 106 | 0 | -15 | 0 | 106 | 0 | 15 | 0
5L4 | Lattice | Basin Electric Power Co-op | California, North Dakota, South Dakota, Colorado, Montana, New Mexico, Wyoming, Minnesota, Iowa | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 85 | 69.2889 | 69.2889 | 0 | -28 | 28 | 99 | -26 | 99 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 100.7111 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -28 | 0 | 28 | 0 | 99 | 0 | -26 | 0 | 99 | 0 | 26 | 0
5L5 | Lattice | Carolina Power & Light Co | North Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 105 | 89.2889 | 89.2889 | 0 | -30.25 | 30.25 | 122.5 | -15.5 | 122.5 | 15.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120.7111 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -30 | -3 | 30 | 3 | 122 | 6 | -15.5 | 0 | 122 | 6 | 15.5 | 0
5L6 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 64.2889 | 64.2889 | 64.2889 | 0 | -35 | 35 | 95 | -25 | 95 | 25 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 95 | 0 | -25 | 0 | 95 | 0 | 25 | 0
5L7 | Lattice | Alabama Power Company, Baltimore Gas and Electric Company | Alabama, Maryland, | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -34 | 34 | 124 | -31 | 124 | 31 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -34 | 0 | 34 | 0 | 124 | 0 | -31 | 0 | 124 | 0 | 31 | 0
5L8 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -33 | 33 | 129 | -20 | 129 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -33 | 0 | 33 | 0 | 129 | 0 | -20 | 0 | 129 | 0 | 20 | 0
5L9 | Lattice | American Electric Power Co, Arizona Public Service Co, Duke Power Company | Virginia, Arizona, South Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 79.2889 | 79.2889 | 79.2889 | 0 | -32 | 32 | 109 | -24 | 109 | 24 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 0 | 0 | -32 | 0 | 32 | 0 | 109 | 0 | -24 | 0 | 109 | 0 | 24 | 0
5L10 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -35 | 35 | 137 | -26 | 137 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 137 | 0 | -26 | 0 | 137 | 0 | 26 | 0
5L11 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 100.2889 | 131.2889 | -15 | -25 | -15 | 172 | 0 | 0 | 0 | 131.2889 | 100.2889 | 69.2889 | 15 | 25 | 15 | 85 | 0 | 116 | 0 | 147 | 0 | -15 | 0 | -25 | 0 | -15 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 116 | 0 | 85 | 0 | 15 | 0 | 25 | 0 | 15 | 0
5L12 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 114.2889 | 69.2889 | 69.2889 | -27.75 | -40.5 | -15 | 150 | -18.5 | 150 | 18.5 | 114.2889 | 69.2889 | 69.2889 | 27.75 | 15 | 40.5 | 130 | 0 | 85 | 0 | 85 | 0 | -27 | -9 | -40 | -6 | -15 | 0 | 150 | 0 | -18.5 | 0 | 150 | 0 | 18.5 | 0 | 130 | 0 | 85 | 0 | 85 | 0 | 27 | 9 | 15 | 0 | 40 | 6
5L13 | Lattice |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 112.2889 | 74.2889 | 74.2889 | -18.5 | -46.5 | -18.5 | 140 | -12.125 | 140 | 15.125 | 112.2889 | 74.2889 | 74.2889 | 18.5 | 18.5 | 46.5 | 128 | 0 | 90 | 0 | 90 | 0 | -18 | -6 | -46 | -6 | -18 | -6 | 140 | 0 | -12 | -1.5 | 140 | 0 | 15 | 1.5 | 128 | 0 | 90 | 0 | 90 | 0 | 18 | 6 | 18 | 6 | 46 | 6
5L14 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | -42 | 0 | 42 | 128 | -21.8333 | 128 | 21.8333 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -42 | 0 | 0 | 0 | 42 | 0 | 128 | 0 | -21 | -10 | 128 | 0 | 21 | 10
5P1 | Pole |  |  | 1 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 99.2889 | 129.2889 | 18 | 21 | 18 | 160 | 4 | 0 | 0 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 85 | 0 | 115 | 0 | 145 | 0 | 18 | 0 | 21 | 0 | 18 | 0 | 160 | 0 | 4 | 0 | 0 | 0 | 0 | 0
5P2 | Pole |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 60.7056 | 73.2889 | 85.7056 | 18 | -17 | 18 | 120 | -10 | 120 | 10 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 77 | -7 | 90 | -12 | 102 | -7 | 18 | 0 | -17 | 0 | 18 | 0 | 120 | 0 | -10 | 0 | 120 | 0 | 10 | 0
5H1 | H frame | Baltimore Gas and Electric Company, Baltimore Gas and Electric Company | Maryland, Maryland | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 104.2889 | 104.2889 | 104.2889 | -35 | 0 | 35 | 129 | -26 | 129 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | -35 | 0 | 0 | 0 | 35 | 0 | 129 | 0 | -26 | 0 | 129 | 0 | 26 | 0
5H2 | H frame |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 123 | 87 | 87 | -30 | -45 | -15 | 149 | -32 | 149 | 32 | 123 | 87 | 87 | 15 | 45 | 15 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | -30 | 0 | -45 | 0 | -15 | 0 | 149 | 0 | -32 | 0 | 149 | 0 | 32 | 0 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | 15 | 0 | 45 | 0 | 15 | 0
5Y1 | Y |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 106.25 | 139.25 | 106.25 | -21.5 | 0 | 21.5 | 153 | -13.75 | 153 | 13.75 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 122.7111 | -9 | 155.7111 | -9 | 122.7111 | -9 | -21 | -6 | 0 | 0 | 21 | 6 | 153 | 0 | -13 | -9 | 153 | 0 | 13 | 9
5Y2 | Y | Arkansas Power & Light Co. | Arkansas | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 118.5 | 88 | 88 | 0 | -21.5 | 21.5 | 131.5 | -20 | 131.5 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 133.7111 | 6 | 103.7111 | 0 | 103.7111 | 0 | 0 | 0 | -21 | -6 | 21 | 6 | 131 | 6 | -20 | 0 | 131 | 6 | 20 | 0
5Y3 | Y | Alabama Power Company | Alabama | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 151.25 | 126 | 126 | 0 | -21 | 21 | 165.25 | -17.5 | 165.25 | 17.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 166.7111 | 3 | 141.7111 | 0 | 141.7111 | 0 | 0 | 0 | -21 | 0 | 21 | 0 | 165 | 3 | -17 | -6 | 165 | 3 | 17 | 6
7L1 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 92 | 92 | 92 | -44.5 | 0 | 44.5 | 127 | -36 | 127 | 36 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 115.0953 | 0 | 115.0953 | 0 | 115.0953 | 0 | -44 | -6 | 0 | 0 | 44 | 6 | 127 | 0 | -36 | 0 | 127 | 0 | 36 | 0
7L2 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 86.9047 | 86.9047 | 86.9047 | -45 | 0 | 45 | 138.6667 | -50 | 138.6667 | 50 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -45 | 0 | 0 | 0 | 45 | 0 | 138 | 8 | -50 | 0 | 138 | 8 | 50 | 0
7L3 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 135 | 135 | 135 | -41.8333 | 0 | 41.8333 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 158.0953 | 0 | 158.0953 | 0 | 158.0953 | 0 | -41 | -10 | 0 | 0 | 41 | 10 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7P1 | Pole |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 100.9047 | 100.9047 | 100.9047 | -39.3333 | 0 | 39.3333 | 145 | -66 | 145 | 66 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 124 | 0 | 124 | 0 | 124 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 145 | 0 | -66 | 0 | 145 | 0 | 66 | 0
7H1 | H frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 131 | 131 | 131 | -50 | 0 | 50 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 154.0953 | 0 | 154.0953 | 0 | 154.0953 | 0 | -50 | 0 | 0 | 0 | 50 | 0 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7V1 | V frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 110 | 110 | 110 | -39.3333 | 0 | 39.3333 | 150 | -30 | 150 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 133.0953 | 0 | 133.0953 | 0 | 133.0953 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 150 | 0 | -30 | 0 | 150 | 0 | 30 | 0
DC1 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0
DC2 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0