## TL_Geometry
code | structure_type | company | state | n_circuits | n_ground_w | voltage_kv | Creep_Dist_mm_kv | Insul_Creep_Dist_mm | Insul_Spac_mm | L_Ins_String_ft | ha1t_ft | hb1t_ft | hc1t_ft | Sa1t_ft | Sb1t_ft | Sc1t_ft | hg11t_ft | Sg11t_ft | hg21t_ft | Sg21t_ft | ha2t_ft | hb2t_ft | hc2t_ft | Sa2t_ft | Sb2t_ft | Sc2t_ft | ha1 (ft) | ha1 (inch) | hb1 (ft) | hb1 (inch) | hc1 (ft) | hc1 (inch) | Sa1 (ft) | Sa1 (inch) | Sb1 (ft) | Sb1 (inch) | Sc1 (ft) | Sc1 (inch) | hg11 (ft) | hg11 (inch) | Sg11 (ft) | Sg11 (inch) | hg21 (ft) | hg21 (inch) | Sg21 (ft) | Sg21 (inch) | ha2 (ft) | ha2 (inch) | hb2 (ft) | hb2 (inch) | hc2 (ft) | hc2 (inch) | Sa2 (ft) | Sa2 (inch) | Sb2 (ft) | Sb2 (inch) | Sc2 (ft) | Sc2 (inch)
3L1 | Lattice | Iowa Public Service Co | Iowa | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -23.75 | 0 | 23.75 | 87.5 | -17.8125 | 87.5 | 17.8125 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -23 | -9 | 0 | 0 | 23 | 9 | 87 | 6 | -17.25 | -6.75 | 87 | 6 | 17.25 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L2 | Lattice | Indianapolis Power and Light Company, Western Power Area Administration | Indiana, Colorado, Colorado | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -32 | 0 | 32 | 96.5 | -21.5 | 96.5 | 21.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -32 | 0 | 0 | 0 | 32 | 0 | 96 | 6 | -21 | -6 | 96 | 6 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L3 | Lattice | Consumers Power Company | Michigan | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 59.1594 | 59.1594 | -24.5 | 0 | 24.5 | 87.5 | -16.5 | 87.5 | 16.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | -24 | -6 | 0 | 0 | 24 | 6 | 87 | 6 | -16 | -6 | 87 | 6 | 16 | 6
3L4 | Lattice | Pennsylvania Electric Co | Pennsylvania | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.1594 | 44.1594 | 44.1594 | -22.6667 | 0 | 22.6667 | 73 | -18.5833 | 73 | 18.5833 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 0 | 55 | 0 | 55 | 0 | -22 | -8 | 0 | 0 | 22 | 8 | 73 | 0 | -18 | -7 | 73 | 0 | 18 | 7
3L5 | Lattice | Northern Indiana Public Service | Indiana | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 79.1594 | 79.1594 | 79.1594 | -24 | 0 | 24 | 102 | -21.6 | 102 | 21.6 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 90 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 102 | 0 | -21.6 | 0 | 102 | 0 | 21.6 | 0
3L6 | Lattice | Cleveland electric iluminating | Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 43.6594 | 43.6594 | 43.6594 | -23 | 0 | 23 | 94.5 | -20.5 | 94.5 | 20.5 | 72.1594 | 72.1594 | 72.1594 | 23 | 0 | -23 | 54 | 6 | 54 | 6 | 54 | 6 | -23 | 0 | 0 | 0 | 23 | 0 | 93 | 18 | -20 | -6 | 93 | 18 | 20 | 6 | 82 | 12 | 82 | 12 | 82 | 12 | 23 | 0 | 0 | 0 | -23 | 0
3L7 | Lattice | Consolidated Edison Co | New York | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 41.826 | 64.826 | 87.826 | -19 | -17.5 | -15.3333 | 104.6667 | -12 | 104.6667 | 12 | 87.826 | 64.826 | 41.826 | 15.3333 | 17.5 | 19 | 52 | 8 | 75 | 8 | 98 | 8 | -19 | 0 | -17 | -6 | -15 | -4 | 104 | 8 | -12 | 0 | 104 | 8 | 12 | 0 | 98 | 8 | 75 | 8 | 52 | 8 | 15 | 4 | 17 | 6 | 19 | 0
3L8 | Lattice | Oklahoma Gas & Electric Co, American Electric Power Co | Michigan, Oklahoma | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 93.1594 | 117.1594 | -22 | -37 | -22 | 142 | -11 | 142 | 11 | 117.1594 | 93.1594 | 69.1594 | 22 | 37 | 22 | 80 | 0 | 104 | 0 | 128 | 0 | -22 | 0 | -37 | 0 | -22 | 0 | 142 | 0 | -11 | 0 | 142 | 0 | 11 | 0 | 128 | 0 | 104 | 0 | 80 | 0 | 22 | 0 | 37 | 0 | 22 | 0
3L9 | Lattice | Consumers Power Company, Indianapolis Power and Light Company | Michigan, Michigan, Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 89.1594 | 111.1594 | -18 | -29 | -17 | 137 | -24 | 137 | 24 | 111.1594 | 89.1594 | 69.1594 | 17 | 29 | 18 | 80 | 0 | 100 | 0 | 122 | 0 | -18 | 0 | -29 | 0 | -17 | 0 | 137 | 0 | -24 | 0 | 137 | 0 | 24 | 0 | 122 | 0 | 100 | 0 | 80 | 0 | 17 | 0 | 29 | 0 | 18 | 0
3L10 | Lattice | Detroit Edison | Michigan | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 53.1594 | 74.6594 | 98.6594 | -20.5 | -27 | -18.5 | 119.5 | -25.75 | 119.5 | 25.75 | 98.6594 | 74.6594 | 53.1594 | 18.5 | 27 | 20.5 | 64 | 0 | 85 | 6 | 109 | 6 | -20 | -6 | -27 | 0 | -18 | -6 | 119 | 6 | -25 | -9 | 119 | 6 | 25 | 9 | 109 | 6 | 85 | 6 | 64 | 0 | 18 | 6 | 27 | 0 | 20 | 6
3L11 | Lattice | Boston Edison Company, Consolidated Edison Co of New York, Houston Lightning Company | Massachusetts, New York, Texas, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 39.1594 | 61.1594 | 83.1594 | -25 | -25 | -25 | 98.5 | -18 | 98.5 | 18 | 83.1594 | 61.1594 | 39.1594 | -25 | -25 | -25 | 50 | 0 | 72 | 0 | 94 | 0 | -25 | 0 | -25 | 0 | -25 | 0 | 98 | 6 | -18 | 0 | 98 | 6 | 18 | 0 | 94 | 0 | 72 | 0 | 50 | 0 | -25 | 0 | -25 | 0 | -25 | 0
3L12 | Lattice | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 61.6594 | 89.6594 | 117.6594 | -15 | -20 | -15 | 136 | -9 | 136 | 9 | 117.6594 | 89.6594 | 61.6594 | 15 | 20 | 15 | 72 | 6 | 100 | 6 | 128 | 6 | -15 | 0 | -20 | 0 | -15 | 0 | 136 | 0 | -9 | 0 | 136 | 0 | 9 | 0 | 128 | 6 | 100 | 6 | 72 | 6 | 15 | 0 | 20 | 0 | 15 | 0
3L13 | Lattice | Union electric company | Missouri | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 91.1594 | 65.1594 | 65.1594 | -17.6667 | -37 | -17 | 109 | -23.3333 | 109 | 23.3333 | 91.1594 | 65.1594 | 65.1594 | 17.6667 | 17 | 37 | 102 | 0 | 76 | 0 | 76 | 0 | -17 | -8 | -37 | 0 | -17 | 0 | 109 | 0 | -23 | -4 | 109 | 0 | 23 | 4 | 102 | 0 | 76 | 0 | 76 | 0 | 17 | 8 | 17 | 0 | 37 | 0
3L14 | Lattice | Texas electric service & Light Co | Texas, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 77.1594 | 52.1594 | 52.1594 | -25.5833 | -37.8333 | -14.3333 | 103 | -15.6667 | 103 | 15.6667 | 77.1594 | 52.1594 | 52.1594 | 25.5833 | 14.3333 | 37.8333 | 88 | 0 | 63 | 0 | 63 | 0 | -25 | -7 | -37 | -10 | -14 | -4 | 103 | 0 | -15 | -8 | 103 | 0 | 15 | 8 | 88 | 0 | 63 | 0 | 63 | 0 | 25 | 7 | 14 | 4 | 37 | 10
3L15 | Lattice | Commonwealth Edison Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 97.1594 | 54.1594 | 54.1594 | -28.5 | -40.5 | -16.5 | 117 | -40.5 | 117 | 40.5 | 97.1594 | 54.1594 | 54.1594 | 69 | 16.5 | 81 | 108 | 0 | 65 | 0 | 65 | 0 | -28.5 | 0 | -40.5 | 0 | -16.5 | 0 | 117 | 0 | -40.5 | 0 | 117 | 0 | 40.5 | 0 | 108 | 0 | 65 | 0 | 65 | 0 | 69 | 0 | 16.5 | 0 | 81 | 0
3P1 | Pole | Dayton Power & Light company | Ohio | 1 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 64.1594 | 75.6594 | 87.1594 | 9 | -9 | 9 | 131.5 | 0 | 0 | 0 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 75 | 0 | 86 | 6 | 98 | 0 | 9 | 0 | -9 | 0 | 9 | 0 | 131 | 6 | 0 | 0 | 0 | 0 | 0 | 0
3P2 | Pole | Cleveland electric iluminating, Indianapolis Power and Light Company, Northeast Utilities | Ohio, Indiana, Connecticut | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 54.1594 | 77.1594 | 100.1594 | -15 | -15 | -15 | 132 | -14 | 132 | 14 | 100.1594 | 77.1594 | 54.1594 | 15 | 15 | 15 | 65 | 0 | 88 | 0 | 111 | 0 | -15 | 0 | -15 | 0 | -15 | 0 | 132 | 0 | -14 | 0 | 132 | 0 | 14 | 0 | 111 | 0 | 88 | 0 | 65 | 0 | 15 | 0 | 15 | 0 | 15 | 0
3P3 | Pole | Northern States Power Company, Wisconsin Electric Power Co | Minnesota, Wisconsin | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 90.1594 | 115.1594 | -14.25 | -21.25 | -14.25 | 135 | -17 | 135 | 17 | 115.1594 | 90.1594 | 65.1594 | 14.25 | 21.25 | 14.25 | 76 | 0 | 101 | 0 | 126 | 0 | -14 | -3 | -21 | -3 | -14 | -3 | 135 | 0 | -17 | 0 | 135 | 0 | 17 | 0 | 126 | 0 | 101 | 0 | 76 | 0 | 14 | 3 | 21 | 3 | 14 | 3
3P4 | Pole | Consolidated Edison Co, Houston Lightning Company, SouthWestern electric company | New York, Texas, Louisiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 81.1594 | 97.1594 | -11 | -11 | -11 | 111.5 | -8 | 111.5 | 8 | 97.1594 | 81.1594 | 65.1594 | 11 | 11 | 11 | 76 | 0 | 92 | 0 | 108 | 0 | -11 | 0 | -11 | 0 | -11 | 0 | 111 | 6 | -8 | 0 | 111 | 6 | 8 | 0 | 108 | 0 | 92 | 0 | 76 | 0 | 11 | 0 | 11 | 0 | 11 | 0
3P5 | Pole | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 72 | 97 | 122 | -11 | -19 | -11 | 140 | -7 | 140 | 7 | 122 | 97 | 72 | 11 | 19 | 11 | 82.8406 | 0 | 107.8406 | 0 | 132.8406 | 0 | -11 | 0 | -19 | 0 | -11 | 0 | 140 | 0 | -7 | 0 | 140 | 0 | 7 | 0 | 132.8406 | 0 | 107.8406 | 0 | 82.8406 | 0 | 11 | 0 | 19 | 0 | 11 | 0
3P6 | Pole | Dayton Power & Light company | Ohio | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 81.6594 | 104.1594 | -9 | -13 | -9 | 145.5 | 0 | 0 | 0 | 104.1594 | 81.6594 | 59.1594 | -9 | -13 | -9 | 70 | 0 | 92 | 6 | 114 | 12 | -9 | 0 | -13 | 0 | -9 | 0 | 144 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 12 | 92 | 6 | 70 | 0 | -9 | 0 | -13 | 0 | -9 | 0
3P7 | Pole | Illinois Power Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.826 | 80.826 | 80.826 | -15.5 | -41 | -16 | 127.6667 | -30 | 127.6667 | 30 | 116.826 | 80.826 | 80.826 | 15.5 | 16 | 41 | 127 | 8 | 91 | 8 | 91 | 8 | -15 | -6 | -41 | 0 | -16 | 0 | 127 | 8 | -30 | 0 | 127 | 8 | 30 | 0 | 127 | 8 | 91 | 8 | 91 | 8 | 15 | 6 | 16 | 0 | 41 | 0
3P8 | Pole | Commonwealth Edison Company | Illinois | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 98.1594 | 55.1594 | 55.1594 | -22 | -33 | -10 | 118 | 0 | 0 | 0 | 98.1594 | 55.1594 | 55.1594 | 22 | 10 | 33 | 109 | 0 | 66 | 0 | 66 | 0 | -22 | 0 | -33 | 0 | -10 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 66 | 0 | 66 | 0 | 22 | 0 | 10 | 0 | 33 | 0
3H1 | H frame | Public Service Company of New Hampshire | New Hampshire, New Hampshire | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -18 | 0 | 18 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -18 | 0 | 0 | 0 | 18 | 0 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H2 | H frame | Utah Power and Light Company | Utah | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 62.1594 | 62.1594 | 62.1594 | -27 | 0 | 27 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 73 | 0 | 73 | 0 | 73 | 0 | -26 | -12 | 0 | 0 | 26 | 12 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H3 | H frame | Niagara Mohawk Power Corporation, Illinois Power Company, Central Maine Power Co | Maine, Illinois, New York | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.826 | 44.826 | 44.826 | -26 | 0 | 26 | 65.5 | -13 | 65.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 8 | 55 | 8 | 55 | 8 | -26 | 0 | 0 | 0 | 26 | 0 | 64 | 18 | -13 | 0 | 64 | 18 | 13 | 0
3H4 | H frame | Public Service Company of New Hampshire, Northeast Utilities, New York State Electric & Gas, Vermont Electric Company, Wisconsin Public Service Corp | New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 50.1594 | 50.1594 | 50.1594 | -26 | 0 | 26 | 73.5 | -13 | 73.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 61 | 0 | 61 | 0 | 61 | 0 | -26 | 0 | 0 | 0 | 26 | 0 | 73.5 | 0 | -13 | 0 | 73.5 | 0 | 13 | 0
3H5 | H frame | El paso electric company | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 59.1594 | 52.6594 | -27 | 0 | 27 | 78 | -13.5 | 78 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 69 | 12 | 63 | 6 | -26 | -12 | 0 | 0 | 26 | 12 | 77 | 12 | -13.5 | 0 | 77 | 12 | 13.5 | 0
3H6 | H frame | Northern States Power Company, Wisconsin Electric Power Co, Kansas Gas & Electric Co | Kansas, Minnesota | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 46.6594 | 58.1594 | 46.6594 | -28.25 | 0 | 28.25 | 69 | -15.25 | 69 | 15.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 57 | 6 | 68 | 12 | 57 | 6 | -28 | -3 | 0 | 0 | 28 | 3 | 68 | 12 | -15 | -3 | 68 | 12 | 15 | 3
3H7 | H frame | Public Service Company of New Mexico | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -23.5 | 0 | 23.5 | 68.5 | -13.5 | 68.5 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -23 | -6 | 0 | 0 | 23 | 6 | 68 | 6 | -13.5 | 0 | 68 | 6 | 13.5 | 0
3H8 | H frame | Union electric company | Missouri | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 51.1594 | 51.1594 | 51.1594 | -24 | 0 | 24 | 72.5 | -26 | 72.5 | 26 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 62 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 72 | 6 | -26 | 0 | 72 | 6 | 26 | 0
3H9 | H frame | New Englad Electric System | New Hampshire | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 52.6594 | 52.6594 | -20 | 0 | 20 | 74.5 | -9.5 | 74.5 | 9.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 63 | 6 | 63 | 6 | -19 | -12 | 0 | 0 | 19 | 12 | 74 | 6 | -9 | -6 | 74 | 6 | 9 | 6
3H10 | H frame | Boston Edison Company | Massachusetts | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 96 | 70 | 70 | -10 | -32.75 | -10 | 111 | -27.25 | 111 | 27.25 | 96 | 70 | 70 | 10 | 10 | 32.75 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | -10 | 0 | -32 | -9 | -10 | 0 | 111 | 0 | -27 | -3 | 111 | 0 | 27 | 3 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | 10 | 0 | 10 | 0 | 32 | 9
3Y1 | Y | Tucson Gas & Electric Co | Arizona | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 109.2427 | 84.6594 | 84.6594 | 0 | -15 | 15 | 120.0833 | -13.5 | 120.0833 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 119 | 13 | 95 | 6 | 95 | 6 | 0 | 0 | -15 | 0 | 15 | 0 | 119 | 13 | -13.5 | 0 | 119 | 13 | 13.5 | 0
3Y2 | Y | Pacific Power Light corp | Wyoming | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -13.5 | 13.5 | 127 | -10 | 127 | 10 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -13 | -6 | 13 | 6 | 127 | 0 | -10 | 0 | 127 | 0 | 10 | 0
3Y3 | Y | SouthWestern electric company | Louisiana, Louisiana | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -19.8333 | 19.8333 | 127 | -9 | 127 | 9 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -19.5 | -4 | 19.5 | 4 | 127 | 0 | -9 | 0 | 127 | 0 | 9 | 0
5L1 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 96.7889 | 69.2889 | 69.2889 | 0 | -20 | 20 | 122.25 | -13 | 122.25 | 13 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 112 | 6 | 85 | 0 | 85 | 0 | 0 | 0 | -20 | 0 | 20 | 0 | 121 | 15 | -13 | 0 | 121 | 15 | 13 | 0
5L2 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 98.2889 | 69.2889 | 69.2889 | 0 | -15.3333 | 15.3333 | 121 | -12 | 121 | 12 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 114 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -15 | -4 | 15 | 4 | 121 | 0 | -12 | 0 | 121 | 0 | 12 | 0
5L3 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 90.2889 | 74.2889 | 74.2889 | 0 | -29 | 29 | 106 | -15 | 106 | 15 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 106 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | -29 | 0 | 29 | 0 | 106 | 0 | -15 | 0 | 106 | 0 | 15 | 0
5L4 | Lattice | Basin Electric Power Co-op | California, North Dakota, South Dakota, Colorado, Montana, New Mexico, Wyoming, Minnesota, Iowa | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 85 | 69.2889 | 69.2889 | 0 | -28 | 28 | 99 | -26 | 99 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 100.7111 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -28 | 0 | 28 | 0 | 99 | 0 | -26 | 0 | 99 | 0 | 26 | 0
5L5 | Lattice | Carolina Power & Light Co | North Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 105 | 89.2889 | 89.2889 | 0 | -30.25 | 30.25 | 122.5 | -15.5 | 122.5 | 15.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120.7111 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -30 | -3 | 30 | 3 | 122 | 6 | -15.5 | 0 | 122 | 6 | 15.5 | 0
5L6 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 64.2889 | 64.2889 | 64.2889 | 0 | -35 | 35 | 95 | -25 | 95 | 25 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 95 | 0 | -25 | 0 | 95 | 0 | 25 | 0
5L7 | Lattice | Alabama Power Company, Baltimore Gas and Electric Company | Alabama, Maryland, | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -34 | 34 | 124 | -31 | 124 | 31 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -34 | 0 | 34 | 0 | 124 | 0 | -31 | 0 | 124 | 0 | 31 | 0
5L8 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -33 | 33 | 129 | -20 | 129 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -33 | 0 | 33 | 0 | 129 | 0 | -20 | 0 | 129 | 0 | 20 | 0
5L9 | Lattice | American Electric Power Co, Arizona Public Service Co, Duke Power Company | Virginia, Arizona, South Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 79.2889 | 79.2889 | 79.2889 | 0 | -32 | 32 | 109 | -24 | 109 | 24 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 0 | 0 | -32 | 0 | 32 | 0 | 109 | 0 | -24 | 0 | 109 | 0 | 24 | 0
5L10 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -35 | 35 | 137 | -26 | 137 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 137 | 0 | -26 | 0 | 137 | 0 | 26 | 0
5L11 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 100.2889 | 131.2889 | -15 | -25 | -15 | 172 | 0 | 0 | 0 | 131.2889 | 100.2889 | 69.2889 | 15 | 25 | 15 | 85 | 0 | 116 | 0 | 147 | 0 | -15 | 0 | -25 | 0 | -15 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 116 | 0 | 85 | 0 | 15 | 0 | 25 | 0 | 15 | 0
5L12 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 114.2889 | 69.2889 | 69.2889 | -27.75 | -40.5 | -15 | 150 | -18.5 | 150 | 18.5 | 114.2889 | 69.2889 | 69.2889 | 27.75 | 15 | 40.5 | 130 | 0 | 85 | 0 | 85 | 0 | -27 | -9 | -40 | -6 | -15 | 0 | 150 | 0 | -18.5 | 0 | 150 | 0 | 18.5 | 0 | 130 | 0 | 85 | 0 | 85 | 0 | 27 | 9 | 15 | 0 | 40 | 6
5L13 | Lattice |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 112.2889 | 74.2889 | 74.2889 | -18.5 | -46.5 | -18.5 | 140 | -12.125 | 140 | 15.125 | 112.2889 | 74.2889 | 74.2889 | 18.5 | 18.5 | 46.5 | 128 | 0 | 90 | 0 | 90 | 0 | -18 | -6 | -46 | -6 | -18 | -6 | 140 | 0 | -12 | -1.5 | 140 | 0 | 15 | 1.5 | 128 | 0 | 90 | 0 | 90 | 0 | 18 | 6 | 18 | 6 | 46 | 6
5L14 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | -42 | 0 | 42 | 128 | -21.8333 | 128 | 21.8333 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -42 | 0 | 0 | 0 | 42 | 0 | 128 | 0 | -21 | -10 | 128 | 0 | 21 | 10
5P1 | Pole |  |  | 1 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 99.2889 | 129.2889 | 18 | 21 | 18 | 160 | 4 | 0 | 0 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 85 | 0 | 115 | 0 | 145 | 0 | 18 | 0 | 21 | 0 | 18 | 0 | 160 | 0 | 4 | 0 | 0 | 0 | 0 | 0
5P2 | Pole |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 60.7056 | 73.2889 | 85.7056 | 18 | -17 | 18 | 120 | -10 | 120 | 10 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 77 | -7 | 90 | -12 | 102 | -7 | 18 | 0 | -17 | 0 | 18 | 0 | 120 | 0 | -10 | 0 | 120 | 0 | 10 | 0
5H1 | H frame | Baltimore Gas and Electric Company, Baltimore Gas and Electric Company | Maryland, Maryland | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 104.2889 | 104.2889 | 104.2889 | -35 | 0 | 35 | 129 | -26 | 129 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | -35 | 0 | 0 | 0 | 35 | 0 | 129 | 0 | -26 | 0 | 129 | 0 | 26 | 0
5H2 | H frame |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 123 | 87 | 87 | -30 | -45 | -15 | 149 | -32 | 149 | 32 | 123 | 87 | 87 | 15 | 45 | 15 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | -30 | 0 | -45 | 0 | -15 | 0 | 149 | 0 | -32 | 0 | 149 | 0 | 32 | 0 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | 15 | 0 | 45 | 0 | 15 | 0
5Y1 | Y |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 106.25 | 139.25 | 106.25 | -21.5 | 0 | 21.5 | 153 | -13.75 | 153 | 13.75 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 122.7111 | -9 | 155.7111 | -9 | 122.7111 | -9 | -21 | -6 | 0 | 0 | 21 | 6 | 153 | 0 | -13 | -9 | 153 | 0 | 13 | 9
5Y2 | Y | Arkansas Power & Light Co. | Arkansas | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 118.5 | 88 | 88 | 0 | -21.5 | 21.5 | 131.5 | -20 | 131.5 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 133.7111 | 6 | 103.7111 | 0 | 103.7111 | 0 | 0 | 0 | -21 | -6 | 21 | 6 | 131 | 6 | -20 | 0 | 131 | 6 | 20 | 0
5Y3 | Y | Alabama Power Company | Alabama | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 151.25 | 126 | 126 | 0 | -21 | 21 | 165.25 | -17.5 | 165.25 | 17.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 166.7111 | 3 | 141.7111 | 0 | 141.7111 | 0 | 0 | 0 | -21 | 0 | 21 | 0 | 165 | 3 | -17 | -6 | 165 | 3 | 17 | 6
7L1 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 92 | 92 | 92 | -44.5 | 0 | 44.5 | 127 | -36 | 127 | 36 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 115.0953 | 0 | 115.0953 | 0 | 115.0953 | 0 | -44 | -6 | 0 | 0 | 44 | 6 | 127 | 0 | -36 | 0 | 127 | 0 | 36 | 0
7L2 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 86.9047 | 86.9047 | 86.9047 | -45 | 0 | 45 | 138.6667 | -50 | 138.6667 | 50 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -45 | 0 | 0 | 0 | 45 | 0 | 138 | 8 | -50 | 0 | 138 | 8 | 50 | 0
7L3 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 135 | 135 | 135 | -41.8333 | 0 | 41.8333 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 158.0953 | 0 | 158.0953 | 0 | 158.0953 | 0 | -41 | -10 | 0 | 0 | 41 | 10 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7P1 | Pole |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 100.9047 | 100.9047 | 100.9047 | -39.3333 | 0 | 39.3333 | 145 | -66 | 145 | 66 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 124 | 0 | 124 | 0 | 124 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 145 | 0 | -66 | 0 | 145 | 0 | 66 | 0
7H1 | H frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 131 | 131 | 131 | -50 | 0 | 50 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 154.0953 | 0 | 154.0953 | 0 | 154.0953 | 0 | -50 | 0 | 0 | 0 | 50 | 0 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7V1 | V frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 110 | 110 | 110 | -39.3333 | 0 | 39.3333 | 150 | -30 | 150 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 133.0953 | 0 | 133.0953 | 0 | 133.0953 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 150 | 0 | -30 | 0 | 150 | 0 | 30 | 0
DC1 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0
DC2 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0

## Neighboring
number | state | abreviation | bordering_states | n_bordering_states
1 | Alabama | AL | Mississippi, Tennessee, Florida, Georgia | 4
2 | Alaska | AK | None | 0
3 | Arizona | AZ | Nevada, New Mexico, Utah, California, Colorado | 5
4 | Arkansas | AR | Oklahoma, Tennessee, Texas, Louisiana, Mississippi, Missouri | 6
5 | California | CA | Oregon, Arizona, Nevada | 3
6 | Colorado | CO | New Mexico, Oklahoma, Utah, Wyoming, Arizona, Kansas, Nebraska | 7
7 | Connecticut | CT | New York, Rhode Island, Massachusetts | 3
8 | Delaware | DE | New Jersey, Pennsylvania, Maryland | 3
9 | Florida | FL | Georgia, Alabama | 2
10 | Georgia | GA | North Carolina, South Carolina, Tennessee, Alabama, Florida | 5
11 | Hawaii | HI | None | 0
12 | Idaho | ID | Utah, Washington, Wyoming, Montana, Nevada, Oregon | 6
13 | Illinois | IL | Kentucky, Missouri, Wisconsin, Indiana, Iowa, Michigan (water border only) | 6
14 | Indiana | IN | Michigan, Ohio, Illinois, Kentucky | 4
15 | Iowa | IA | Nebraska, South Dakota, Wisconsin, Illinois, Minnesota, Missouri | 6
16 | Kansas | KS | Nebraska, Oklahoma, Colorado, Missouri | 4
17 | Kentucky | KY | Tennessee, Virginia, West Virginia, Illinois, Indiana, Missouri, Ohio | 7
18 | Louisiana | LA | Texas, Arkansas, Mississippi | 3
19 | Maine | ME | New Hampshire | 1
20 | Maryland | MD | Virginia, West Virginia, Delaware, Pennsylvania | 4
21 | Massachusetts | MA | New York, Rhode Island, Vermont, Connecticut, New Hampshire | 5
22 | Michigan | MI | Ohio, Wisconsin, Illinois, Indiana, Minnesota (water border) | 5
23 | Minnesota | MN | North Dakota, South Dakota, Wisconsin, Iowa, Michigan (water border) | 5
24 | Mississippi | MS | Louisiana, Tennessee, Alabama, Arkansas | 4
25 | Missouri | MO | Nebraska, Oklahoma, Tennessee, Arkansas, Illinois, Iowa, Kansas, Kentucky | 8
26 | Montana | MT | South Dakota, Wyoming, Idaho, North Dakota | 4
27 | Nebraska | NE | Missouri, South Dakota, Wyoming, Colorado, Iowa, Kansas, | 6
28 | Nevada | NV | Idaho, Oregon, Utah, Arizona, California | 5
29 | New Hampshire | NH | Vermont, Maine, Massachusetts | 3
30 | New Jersey | NJ | Pennsylvania, Delaware, New York | 3
31 | New Mexico | NM | Oklahoma, Texas, Utah, Arizona, Colorado | 5
32 | New York | NY | Pennsylvania, Rhode Island (water border), Vermont, Connecticut, Massachusetts, New Jersey | 6
33 | North Carolina | NC | Tennessee, Virginia, Georgia, South Carolina | 4
34 | North Dakota | ND | South Dakota, Minnesota, Montana | 3
35 | Ohio | OH | Michigan, Pennsylvania, West Virginia, Indiana, Kentucky | 5
36 | Oklahoma | OK | Missouri, New Mexico, Texas, Arkansas, Colorado, Kansas | 6
37 | Oregon | OR | Nevada, Washington, California, Idaho | 4
38 | Pennsylvania | PA | New York, Ohio, West Virginia, Delaware, Maryland, New Jersey | 6
39 | Rhode Island | RI | Massachusetts, New York (water border), Connecticut | 3
40 | South Carolina | SC | North Carolina, Georgia, | 2
41 | South Dakota | SD | Nebraska, North Dakota, Wyoming, Iowa, Minnesota, Montana | 6
42 | Tennessee | TN | Mississippi, Missouri, North Carolina, Virginia, Alabama, Arkansas, Georgia, Kentucky | 8
43 | Texas | TX | New Mexico, Oklahoma, Arkansas, Louisiana | 4
44 | Utah | UT | Nevada, New Mexico, Wyoming, Arizona, Colorado, Idaho | 6
45 | Vermont | VT | New Hampshire, New York, Massachusetts | 3
46 | Virginia | VA | North Carolina, Tennessee, West Virginia, Kentucky, Maryland | 5
47 | Washington | WA | Oregon, Idaho | 2
48 | West Virginia | WV | Pennsylvania, Virginia, Kentucky, Maryland, Ohio | 5
49 | Wisconsin | WI | Michigan, Minnesota, Illinois, Iowa | 4
50 | Wyoming | WY | Nebraska, South Dakota, Utah, Colorado, Idaho, Montana | 6

## TL_data_set
code | structure_type | company | state | miles | voltage_kv | conductor_type | conductor_name | Flag_cond_dataset | conductor_diameter_inch | conductor_kcmil | conductor_stranding | bundling | bundling_spacing_inch | ground_Type | ground_diameter_inch | ground_kcmil |  | concatenation | 3L1 | 3L2 | 3L3 | 3L4 | 3L5 | 3L6 | 3L7 | 3L8 | 3L9 | 3L10 | 3L11 | 3L12 | 3L13 | 3L14 | 3L15 | 3P1 | 3P2 | 3P3 | 3P4 | 3P5 | 3P6 | 3P7 | 3P8 | 3H1 | 3H2 | 3H3 | 3H4 | 3H5 | 3H6 | 3H7 | 3H8 | 3H9 | 3H10 | 3Y1 | 3Y2 | 3Y3 | 5L1 | 5L2 | 5L3 | 5L4 | 5L5 | 5L6 | 5L7 | 5L8 | 5L9 | 5L10 | 5L11 | 5L12 | 5L13 | 5L14 | 5P1 | 5P2 | 5H1 | 5H2 | 5Y1 | 5Y2 | 5Y3 | 7L1 | 7L2 | 7L3 | 7P1 | 7H1 | 7V1
3L8 | Lattice | American Electric Co. | Michigan | 188 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3L8: Michigan
3L11 | Lattice | Boston Edison Company | Massachusetts | 18 | 345 | ACAR | Lapwing | 1 | 1.504 | 1703 | 48/13 | 2 | 18 | Alumoweld | 0.343 | 117.649 |  | ACARLapwing | 3L11: Massachusetts
3H10 | H Frame | Boston Edison Company | Massachusetts | 33 | 345 | ACSR | Falcon | 1 | 1.545 | 1590 | 54/19 | 2 | 18 | Alumoweld | 0.343 | 117.649 |  | ACSRFalcon | 3H10: Massachusetts
3H3 | H Frame | Central Maine Power Co | Maine | 86.8 | 345 | AAC | Hawthorn | 1 | 1.1 | 1192.5 | 61/0 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | AACHawthorn | 3H3: Maine
3P2 | Pole | Cleveland Electric Iluminating Co | Ohio | 18 | 345 | ACSR | Cardinal | 1 | 1.175 | 954 | 48/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRCardinal | 3P2: Ohio
3L6 | Lattice | Cleveland Electric Iluminating Co | Ohio | 44 | 345 | ACSR | Cardinal | 1 | 1.175 | 957 | 48/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRCardinal | 3L6: Ohio
3L15 | Lattice | Commonwealth Edison Company | Illinois | 104 | 345 | ACAR | Bunting | 1 | 1.302 | 1277 | 54/7 | 2 | 18 | Alumoweld | 0.349 | 121.801 |  | ACARBunting | 3L15: Illinois
3P8 | Pole | Commonwealth Edison Company | Illinois | 54 | 345 | ACAR | Bunting | 1 | 1.302 | 1277 | 54/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACARBunting | 3P8: Illinois
3P4 | Pole | Consolidated Edison Co of New York | New York | 19 | 345 | ACAR | Kingfisher | 1 | 1.821 | 2500 | 54/37 | 2 | 18 | Alumoweld | 0.5625 | 316.4062 |  | ACARKingfisher | 3P4: New York
3L11 | Lattice | Consolidated Edison Co of New York | New York | 25 | 345 | ACAR | Kingfisher | 1 | 1.821 | 2500 | 54/37 | 2 | 18 | Alumoweld | 0.5625 | 316.4062 |  | ACARKingfisher | 3L11: New York
3L7 | Lattice | Consolidated Edison Co of New York | New York | 150 | 345 | ACSR | Kiwi | 1 | 1.82 | 2167 | 72/7 | 2 | 18 | Alumoweld | 0.5625 | 316.4062 |  | ACSRKiwi | 3L7: New York
3L3 | Lattice | Consumers Power Company | Michigan | 253 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3L3: Michigan
3L9 | Lattice | Consumers Power Company | Michigan | 377 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3L9: Michigan
3L9 | Lattice | Consumers Power Company | Michigan | 161.6 | 345 | ACSR | Bobolink | 1 | 1.427 | 1431 | 45/7 | 2 | 18 | Steel | 0.4375 | 191.4062 | 7/16 | ACSRBobolink | 3L9: Michigan
3P6 | Pole | Dayton Power & Light Company | Ohio | 24.5 | 345 | ACAR | Rail | 1 | 1.165 | 1024.5 | 30/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACARRail | 3P6: Ohio
3P1 | Pole | Dayton Power & Light Company | Ohio | 21.8 | 345 | ACAR | Rail | 1 | 1.165 | 1024.5 | 30/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACARRail | 3P1: Ohio
3L10 | Lattice | Detroit Edison | Michigan | 130 | 345 | ACSR | Bobolink | 1 | 1.427 | 1431 | 45/7 | 2 | 18 | ACSR | 0.576 | 331.776 |  | ACSRBobolink | 3L10: Michigan
3H5 | H Frame | El Paso Electric Copany | New Mexico | 230 | 345 | ACSR | Tern | 1 | 1.063 | 795 | 45/7 | 2 | 18 | Galv Steel | 0.375 | 140.625 | 3/8 | ACSRTern | 3H5: New Mexico
3P4 | Pole | Houston Lightinh & Power Company | Texas | 1.6 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3P4: Texas
3L11 | Lattice | Houston Lightinh & Power Company | Texas | 18 | 345 | ACSR | Kiwi | 1 | 1.737 | 2167 | 72/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRKiwi | 3L11: Texas
3L11 | Lattice | Houston Lightinh & Power Company | Texas | 46 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L11: Texas
3H3 | H Frame | Illinois Power Company | Illinois | 356 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Alumoweld | 0.385 | 148.225 |  | ACSRBluebird | 3H3: Illinois
3P7 | Pole | Illinois Power Company | Illinois | 15.5 | 345 | ACSR | Falcon | 1 | 1.293 | 1590 | 54/19 | 2 | 18 | Alumoweld | 0.433 | 187.489 |  | ACSRFalcon | 3P7: Illinois
3L2 | Lattice | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3L2: Indiana
3L9 | Lattice | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3L9: Indiana
3P2 | Pole | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRRail | 3P2: Indiana
3L1 | Lattice | Iowa Public Service Co | Iowa | 76 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L1: Iowa
3H6 | H Frame | Kansas Gas & Electric Co | Kansas | 600 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRRail | 3H6: Kansas
3H9 | H Frame | New Englad Electric System | New Hampshire | 36 | 345 | AAC | Marigold | 1 | 1.216 | 1113 | 61/0 | 2 | 16 | Alumoweld | 0.343 | 117.649 |  | AACMarigold | 3H9: New Hampshire
3H4 | H Frame | New York State Electric & Gas | New York | 220 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3H4: New York
3H4 | H Frame | New York State Electric & Gas | New York | 56.9 | 345 | ACSR | Ortolan | 1 | 1.212 | 1033.5 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSROrtolan | 3H4: New York
3H3 | H Frame | Niagara Mohawk Power Corp. | New York | 83 | 345 | ACSR | Bunting | 1 | 1.302 | 1192.5 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRBunting | 3H3: New York
3H4 | H Frame | Northeast Utilities | Connecticut | 275 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.375 | 140.625 |  | ACSRRail | 3H4: Connecticut
3P2 | Pole | Northeast Utilities | Connecticut | 11.8 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | Alumoweld | 0.375 | 140.625 |  | ACSRBittern | 3P2: Connecticut
3L5 | Lattice | Northern Indiana Public Service Co | Indiana | 19.45 | 345 | ACSR | Bluebird | 1 | 1.762 | 3104.644 | 84/19 | 1 | 0 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRBluebird | 3L5: Indiana
3H6 | H Frame | Northern States Power Company | Minnesota | 336.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3H6: Minnesota
3P3 | Pole | Northern States Power Company | Minnesota | 96.4 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRCardinal | 3P3: Minnesota
3L8 | Lattice | Oklahoma Gas & Electric Co. | Oklahoma | 230.9 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L8: Oklahoma
3Y2 | Y | Pacific Power & Light Co. | Wyoming | 471.2 | 345 | ACSR | Skylark | 1 | 1.316 | 1272 | 36/1 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRSkylark | 3Y2: Wyoming
3L4 | Lattice | Pennsylvania Electric Co. | Pennsylvania | 27.3 | 345 | ACSR | Curlew | 1 | 1.246 | 1033.5 | 54/7 | 2 | 18 | EHS steel | 15.5 | 240250 | 3/8 | ACSRCurlew | 3L4: Pennsylvania
3H4 | H Frame | Public Service Company of New Hampshire | New Hampshire | 23.6 | 345 | ACSR | Finch | 1 | 1.293 | 1113 | 54/19 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRFinch | 3H4: New Hampshire
3H1 | H Frame | Public Service Company of New Hampshire | New Hampshire | 17 | 345 | ACSR | Finch | 1 | 1.293 | 1113 | 54/19 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRFinch | 3H1: New Hampshire
3H1 | H Frame | Public Service Company of New Hampshire | New Hampshire | 36.4 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 2 | 18 | Alumoweld | 0.385 | 148.225 |  | ACSRBluebird | 3H1: New Hampshire
3H7 | H Frame | Public Service Co. of New Mexico | New Mexico | 160 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3H7: New Mexico
3Y3 | Y | Southwestern Electric Power Company | Louisiana | 64.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | Alumoweld | 0.433 | 187.489 |  | ACSRDrake | 3Y3: Louisiana
3P4 | Pole | Southwestern Electric Power Company | Louisiana | 7.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3P4: Louisiana
3Y3 | Y | Southwestern Electric Power Company | Louisiana | 73.4 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 54/19 | 1 | 0 | Alumoweld | 0.433 | 187.489 |  | ACSRBluebird | 3Y3: Louisiana
3L14 | Lattice | Texas Electric Service Co. | Texas | 240.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3L14: Texas
3L14 | Lattice | Texas Power & Light Co. | Texas | 68.8 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRDrake | 3L14: Texas
3Y1 | Y | Tucson Gas & Electric Co. | Arizona | 413 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRRail | 3Y1: Arizona
3H8 | H Frame | Union Electric Company | Missouri | 186 | 345 | ACSR | Tern | 1 | 1.063 | 795 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRTern | 3H8: Missouri
3L13 | Lattice | Union Electric Company | Missouri | 23 | 345 | ACSR | Lapwing | 1 | 1.504 | 1590 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRLapwing | 3L13: Missouri
3L12 | Lattice | Utah Power and Light Company | Utah | 45 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | EHS steel | 0.5 | 250 | 1/2 | ACSRBittern | 3L12: Utah
3P5 | Pole | Utah Power and Light Company | Utah | 61 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | EHS steel | 0.5 | 250 | 1/2 | ACSRBittern | 3P5: Utah
3H2 | H Frame | Utah Power and Light Company | Utah | 248 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | Alumoweld | 0.475 | 225.625 |  | ACSRCardinal | 3H2: Utah
3H4 | H Frame | Vermont Electric Company | Vermont | 51.3 | 345 | ACAR | Drake | 1 | 1.108 | 927.2 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACARDrake | 3H4: Vermont
3L2 | Lattice | Western Area Power Administration | Colorado | 141 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | Steel | 0.5 | 250 |  | ACSRBittern | 3L2: Colorado
3L2 | Lattice | Western Area Power Administration | Colorado | 419 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16 | ACSRCardinal | 3L2: Colorado
3P3 | Pole | Wisconsin Electric Power Co | Wisconsin | 28 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | ACSR Guinea | 0.576 | 159 |  | ACSRBluebird | 3P3: Wisconsin
3H4 | H Frame | Wisconsin Public Service Corp | Wisconsin | 28.8 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8 | ACSRDrake | 3H4: Wisconsin
[19 empty] | Iowa | Indiana, Colorado, Colorado | Michigan | Pennsylvania | Indiana | Ohio | New York | Michigan, Oklahoma | Michigan, Michigan, Indiana | Michigan | Massachusetts, New York, Texas, Texas | Utah | Missouri | Texas, Texas | Illinois | Ohio | Ohio, Indiana, Connecticut | Minnesota, Wisconsin | New York, Texas, Louisiana | Utah | Ohio | Illinois | Illinois | New Hampshire, New Hampshire | Utah | Maine, Illinois, New York | New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin | New Mexico | Kansas, Minnesota | New Mexico | Missouri | New Hampshire | Massachusetts | Arizona | Wyoming | Louisiana, Louisiana
[19 empty] | Iowa | Indiana, Colorado, Colorado | Michigan | Pennsylvania | Indiana | Ohio | New York | Michigan, Oklahoma | Michigan, Michigan, Indiana | Michigan | Massachusetts, New York, Texas, Texas | Utah | Missouri | Texas, Texas | Illinois | Ohio | Ohio, Indiana, Connecticut | Minnesota, Wisconsin | New York, Texas, Louisiana | Utah | Ohio | Illinois | Illinois | New Hampshire, New Hampshire | Utah | Maine, Illinois, New York | New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin | New Mexico | Kansas, Minnesota | New Mexico | Missouri | New Hampshire | Massachusetts | Arizona | Wyoming | Louisiana, Louisiana
Iowa
Indiana, Colorado, Colorado
Michigan
Pennsylvania
Indiana
Ohio
New York
Michigan, Oklahoma
Michigan, Michigan, Indiana
Michigan
Massachusetts, New York, Texas, Texas
Utah
Missouri
Texas, Texas
Illinois
Ohio
Ohio, Indiana, Connecticut
Minnesota, Wisconsin
New York, Texas, Louisiana
Utah
Ohio
Illinois
Illinois
Illinois
New Hampshire, New Hampshire
Utah
Maine, Illinois, New York
New York, New York, Connecticut, New Hampshire, Vermont, Wisconsin
New Mexico
Kansas, Minnesota
New Mexico
Missouri
New Hampshire
Massachusetts
Arizona
Wyoming
Louisiana, Louisiana

## Conductors
conductor_type | codeword | Size_kcmil | stranding | diameter_inch | R_20DC_ohm_kft | R_25AC_ohm_kft | R_50AC_ohm_kft | R_75AC_ohm_kft | C_60Hz_Mohm_kft | L_60Hz_25C_ohm_kft | Ampacity (A) | Concatenation
ACSR | Waxwing | 266.8 | 18/1 | 0.609 | 0.0644 | 0.0657 | 0.0723 | 0.0788 | 0.576 | 0.0903 | 445 | ACSRWaxwing | 0.47678
ACSR | Partridge | 266.8 | 26/7 | 0.642 | 0.0637 | 0.0652 | 0.0714 | 0.0778 | 0.565 | 0.0881 | 455 | ACSRPartridge | 0.46517
ACSR | Merlin | 336.4 | 18/1 | 0.684 | 0.051 | 0.0523 | 0.0574 | 0.0625 | 0.56 | 0.0826 | 515 | ACSRMerlin | 0.43613
ACSR | Linnet | 336.4 | 26/7 | 0.721 | 0.0506 | 0.0517 | 0.0568 | 0.0619 | 0.549 | 0.0854 | 530 | ACSRLinnet | 0.45091
ACSR | Oriole | 336.4 | 30/7 | 0.741 | 0.0502 | 0.0513 | 0.0563 | 0.0614 | 0.544 | 0.0843 | 530 | ACSROriole | 0.4451
ACSR | Chickadee | 397.5 | 18/1 | 0.743 | 0.0432 | 0.0443 | 0.0487 | 0.0528 | 0.544 | 0.0856 | 575 | ACSRChickadee | 0.45197
ACSR | Ibis | 397.5 | 26/7 | 0.783 | 0.0428 | 0.0438 | 0.0481 | 0.0525 | 0.539 | 0.0835 | 590 | ACSRIbis | 0.44088
ACSR | Pelican | 477 | 18/1 | 0.814 | 0.036 | 0.0369 | 0.0405 | 0.0441 | 0.528 | 0.0835 | 640 | ACSRPelican | 0.44088
ACSR | Flicker | 477 | 24/7 | 0.846 | 0.0358 | 0.0367 | 0.0403 | 0.0439 | 0.524 | 0.0818 | 670 | ACSRFlicker | 0.4319
ACSR | Hawk | 477 | 26/7 | 0.858 | 0.0357 | 0.0366 | 0.0402 | 0.0438 | 0.522 | 0.0814 | 660 | ACSRHawk | 0.42979
ACSR | Hen | 477 | 30/7 | 0.883 | 0.0354 | 0.0362 | 0.0398 | 0.0434 | 0.517 | 0.0803 | 660 | ACSRHen | 0.42398
ACSR | Osprey | 556.5 | 18/1 | 0.879 | 0.0309 | 0.0318 | 0.0348 | 0.0379 | 0.518 | 0.0818 | 710 | ACSROsprey | 0.4319
ACSR | Parakeet | 556.5 | 24/7 | 0.914 | 0.0307 | 0.0314 | 0.0347 | 0.0377 | 0.512 | 0.0801 | 720 | ACSRParakeet | 0.42293
ACSR | Dove | 556.5 | 26/7 | 0.927 | 0.0305 | 0.0314 | 0.0345 | 0.0375 | 0.51 | 0.0795 | 730 | ACSRDove | 0.41976
ACSR | Rook | 636 | 24/7 | 0.977 | 0.0268 | 0.0277 | 0.0303 | 0.033 | 0.502 | 0.0786 | 780 | ACSRRook | 0.41501
ACSR | Grosbeak | 636 | 26/7 | 0.99 | 0.0267 | 0.0275 | 0.0301 | 0.0328 | 0.499 | 0.078 | 790 | ACSRGrosbeak | 0.41184
ACSR | Drake | 795 | 26/7 | 1.108 | 0.0214 | 0.0222 | 0.0242 | 0.0263 | 0.482 | 0.0756 | 910 | ACSRDrake | 0.39917
ACSR | Tern | 795 | 45/7 | 1.063 | 0.0216 | 0.0225 | 0.0246 | 0.0267 | 0.488 | 0.0769 | 890 | ACSRTern | 0.40603
ACSR | Rail | 954 | 45/7 | 1.165 | 0.018 | 0.0188 | 0.0206 | 0.0223 | 0.474 | 0.0748 | 970 | ACSRRail | 0.39494
ACSR | Cardinal | 954 | 54/7 | 1.196 | 0.0179 | 0.0186 | 0.0205 | 0.0222 | 0.47 | 0.0737 | 990 | ACSRCardinal | 0.38914
ACSR | Ortolan | 1033.5 | 45/7 | 1.213 | 0.0167 | 0.0175 | 0.019148 | 0.021 | 0.46728 | 0.073864 | 1030 | ACSROrtolan | 0.39 |  | From Stevenson |  | from prioritywire catalog
ACSR | Curlew | 1033.5 | 54/7 | 1.246 | 0.0165 | 0.0172 | 0.0189 | 0.0205 | 0.464 | 0.0729 | 1040 | ACSRCurlew | 0.38491 |  | Not in ASTM B232
ACSR | Bluejay | 1113 | 45/7 | 1.259 | 0.0155 | 0.0163 | 0.0178 | 0.0193 | 0.461 | 0.0731 | 1070 | ACSRBluejay | 0.38597
ACSR | Finch | 1113 | 54/19 | 1.293 | 0.0155 | 0.016212 | 0.017746 | 0.02 | 0.45725 | 0.07197 | 1070 | ACSRFinch | 0.38 |  | From Stevenson |  | from prioritywire catalog
ACSR | Bittern | 1272 | 45/7 | 1.345 | 0.0135 | 0.0144 | 0.0157 | 0.017 | 0.451 | 0.0716 | 1160 | ACSRBittern | 0.37805
ACSR | Pheasant | 1272 | 54/19 | 1.382 | 0.0135 | 0.014223 | 0.015549 | 0.017 | 0.44722 | 0.070455 | 1180 | ACSRPheasant | 0.372 |  | From Stevenson |  | from prioritywire catalog
ACSR | Bobolink | 1431 | 45/7 | 1.427 | 0.0121 | 0.012955 | 0.014129 | 0.015 | 0.44194 | 0.070265 | 1260 | ACSRBobolink | 0.371 |  | From Stevenson |  | from prioritywire catalog
ACSR | Plover | 1431 | 54/19 | 1.465 | 0.012 | 0.012746 | 0.01392 | 0.016 | 0.43771 | 0.069129 | 1270 | ACSRPlover | 0.365 |  | From Stevenson |  | from prioritywire catalog
ACSR | Lapwing | 1590 | 45/7 | 1.502 | 0.0108 | 0.0117 | 0.0128 | 0.0138 | 0.434 | 0.0689 | 1340 | ACSRLapwing | 0.36379
ACSR | Falcon | 1590 | 54/19 | 1.545 | 0.0108 | 0.0116 | 0.0129 | 0.014 | 0.43 | 0.0678 | 1360 | ACSRFalcon | 0.35798
ACSR | Bluebird | 2156 | 84/19 | 1.762 | 0.00801 | 0.00903 | 0.00977 | 0.0105 | 0.409 | 0.0652 | 1610 | ACSRBluebird | 0.34426
AAC | Laurel | 266.8 | 19/0 | 0.593 | 0.0648 | 0.0663 | 0.0727 | 0.0794 | 0.581 | 0.0648 | 445 | AACLaurel | 0.34214
AAC | Tulip | 336.4 | 19/0 | 0.666 | 0.0513 | 0.0527 | 0.0578 | 0.0629 | 0.56 | 0.0513 | 510 | AACTulip | 0.27086
AAC | Cosmos | 477 | 19/0 | 0.792 | 0.0363 | 0.0373 | 0.0409 | 0.0445 | 0.533 | 0.0363 | 640 | AACCosmos | 0.19166
AAC | Syringa | 477 | 37/0 | 0.795 | 0.0363 | 0.0373 | 0.0409 | 0.0445 | 0.533 | 0.0363 | 640 | AACSyringa | 0.19166
AAC | Zinnia | 500 | 19/0 | 0.811 | 0.0346 | 0.0356 | 0.039 | 0.0426 | 0.533 | 0.0346 | 660 | AACZinnia | 0.18269
AAC | Dahlia | 556.5 | 19/0 | 0.856 | 0.0311 | 0.032 | 0.0352 | 0.0383 | 0.522 | 0.0311 | 700 | AACDahlia | 0.16421
AAC | Orchid | 636 | 37/0 | 0.918 | 0.0272 | 0.0282 | 0.0309 | 0.0335 | 0.511 | 0.0272 | 760 | AACOrchid | 0.14362
AAC | Violet | 715 | 37/0 | 0.974 | 0.0241 | 0.025 | 0.0275 | 0.0299 | 0.502 | 0.0241 | 820 | AACViolet | 0.12725
AAC | Arbutus | 795 | 37/0 | 1.026 | 0.0217 | 0.0227 | 0.0248 | 0.0269 | 0.494 | 0.0217 | 880 | AACArbutus | 0.11458
AAC | Magnolia | 954 | 37/0 | 1.124 | 0.0181 | 0.0191 | 0.0208 | 0.0227 | 0.479 | 0.0181 | 980 | AACMagnolia | 0.095568
AAC | Bluebell | 1033.5 | 37/0 | 1.17 | 0.0167 | 0.0177 | 0.0193 | 0.021 | 0.473 | 0.0167 | 1030 | AACBluebell | 0.088176
AAC | Marigold | 1113 | 61/0 | 1.216 | 0.0155 | 0.0165 | 0.019 | 0.0195 | 0.467 | 0.0744 | 1050 | AACMarigold | 0.39283 | 0.0391
AAC | Columbine | 1351.5 | 61/0 | 1.34 | 0.0128 | 0.0138 | 0.0151 | 0.0163 | 0.452 | 0.0128 | 1210 | AACColumbine | 0.067584
AAC | Coreopsis | 1590 | 61/0 | 1.454 | 0.0128 | 0.012 | 0.013 | 0.0141 | 0.439 | 0.0128 | 1230 | AACCoreopsis | 0.067584
AAC | Cowslip | 2000 | 91/0 | 1.63 | 0.00865 | 0.00994 | 0.0107 | 0.0115 | 0.421 | 0.00865 | 1520 | AACCowslip | 0.045672
AAC | Lupine | 2500 | 91/0 | 1.823 | 0.00699 | 0.00845 | 0.00907 | 0.0097 | 0.404 | 0.00699 | 1700 | AACLupine | 0.036907
AAAC | 1439.2 | 1439.2 | 61/0 |  | 0.014 | 0.014669 | 0.015916 | 0.017167 | 0 | 0 | 897 | AAAC1439.2 |  |  |  | AAAC Ampacity APAR Catalog
AAAC | 1348.8 | 1348.8 | 61/0 |  | 0.01494 | 0.015654 | 0.016985 | 0.018319 | 0 | 0 | 865 | AAAC1348.8
AAAC | 1259.6 | 1259.6 | 61/0 |  | 0.016 | 0.016765 | 0.01819 | 0.019619 | 0 | 0 | 831 | AAAC1259.6
AAAC | 1165.1 | 1165.1 | 61/0 |  | 0.0173 | 0.018127 | 0.019668 | 0.021213 | 0 | 0 | 794 | AAAC1165.1
AAAC | 1077.4 | 1077.4 | 61/0 |  | 0.0187 | 0.019594 | 0.021259 | 0.02293 | 0 | 0 | 760 | AAAC1077.4
AAAC | Greeley | 927.2 | 37/0 | 1.108 | 0.02173 | 0.022769 | 0.024704 | 0.026645 | 0.678 | 0.107 | 694 | AAACGreeley |  |  |  | L,C and d_inch from Cmewire catalog
AAAC | Flint | 740.8 | 37/0 | 0.991 | 0.0272 | 0.028501 | 0.030923 | 0.033352 | 0.715 | 0.112 | 607 | AAACFlint |  |  |  | R from ASTM (dc)
AAAC | Elgin | 652.4 | 19/0 | 0.927 | 0.3089 | 0.32367 | 0.35118 | 0.37877 | 0.751 | 0.118 | 564 | AAACElgin
AAAC | Darien | 559.5 | 19/0 | 0.858 | 0.03602 | 0.037742 | 0.04095 | 0.044167 | 0.522 | 0.0829 | 514 | AAACDarien
AAAC | Cairo | 465.4 | 19/0 | 0.783 | 0.0433 | 0.04537 | 0.049226 | 0.053094 | 0.536 | 0.0851 | 461 | AAACCairo
AAAC | Canton | 394.5 | 19/0 | 0.721 | 0.05107 | 0.053512 | 0.05806 | 0.062622 | 0.549 | 0.087 | 417 | AAACCanton
AAAC | Butte | 312.8 | 19/0 | 0.642 | 0.06443 | 0.067511 | 0.073248 | 0.079003 | 0.567 | 0.0896 | 362 | AAACButte
ACAR | Pelican | 503.6 | 15/4 | 0.814 | 0.0354 | 0.0364 | 0.03985 | 0.0433 | 0.531 | 0.0841 |  | ACARPelican | 0.0257 |  |  | R from ASTM (dc) +3%
ACAR | Osprey | 587.2 | 15/4 | 0.879 | 0.0303 | 0.0312 | 0.03415 | 0.0371 | 0.518 | 0.0824 |  | ACAROsprey | 0.0277
ACAR | Dove | 649.5 | 18/19 | 0.927 | 0.0287 | 0.0295 | 0.0322 | 0.0349 | 0.509 | 0.0812 |  | ACARDove | 0.0292
ACAR | Dove | 653.1 | 12/7 | 0.927 | 0.0279 | 0.0288 | 0.03145 | 0.0341 | 0.509 | 0.0811 | 760 | ACARDove | 0.0293
ACAR | Grosbeak | 739.8 | 18/19 | 0.99 | 0.0252 | 0.0259 | 0.0283 | 0.0307 | 0.499 | 0.0793 | 814 | ACARGrosbeak | 0.0317
ACAR | Tern | 853.7 | 30/7 | 1.063 | 0.0208 | 0.0216 | 0.02365 | 0.0257 | 0.488 | 0.0777 | 907 | ACARTern | 0.034
ACAR | Tern | 853.7 | 24/13 | 1.063 | 0.0213 | 0.0222 | 0.0242 | 0.0262 | 0.488 | 0.0777 |  | ACARTern | 0.034
ACAR | Drake | 927.2 | 24/13 | 1.108 | 0.0208 | 0.0216 | 0.0234 | 0.0252 | 0.482 | 0.0767 |  | ACARDrake | 0.0355
ACAR | Rail | 1024.5 | 30/7 | 1.165 | 0.0173 | 0.0182 | 0.01985 | 0.0215 | 0.474 | 0.0756 | 1015 | ACARRail | 0.0373
ACAR | Rail | 1024.5 | 24/13 | 1.165 | 0.0178 | 0.0186 | 0.02025 | 0.0219 | 0.474 | 0.0756 |  | ACARRail | 0.0373 |  |  | ACAR Ampacity from southwire catalog
ACAR | Cardinal | 1080.6 | 24/13 | 1.196 | 0.0168 | 0.0176 | 0.0192 | 0.0208 | 0.47 | 0.075 |  | ACARCardinal | 0.0383
ACAR | Cardinal | 1080.6 | 18/19 | 1.196 | 0.0172 | 0.0181 | 0.0197 | 0.0213 | 0.47 | 0.075 | 1028 | ACARCardinal | 0.0383
ACAR | Ortolan | 1109 | 30/7 | 1.212 | 0.016 | 0.0169 | 0.0184 | 0.0199 | 0.468 | 0.0747 | 1065 | ACAROrtolan | 0.0388
ACAR | Ortolan | 1109 | 24/13 | 1.212 | 0.0164 | 0.0172 | 0.01875 | 0.0203 | 0.468 | 0.0747 |  | ACAROrtolan | 0.0388
ACAR | Curlew | 1172 | 30/7 | 1.246 | 0.0152 | 0.016 | 0.01745 | 0.0189 | 0.463 | 0.074 | 1101 | ACARCurlew | 0.0399
ACAR | Curlew | 1172 | 18/19 | 1.246 | 0.0159 | 0.0166 | 0.01805 | 0.0195 | 0.463 | 0.074 |  | ACARCurlew | 0.0399
ACAR | Bluejay | 1198 | 30/7 | 1.259 | 0.0148 | 0.0155 | 0.01695 | 0.0184 | 0.462 | 0.0738 | 1115 | ACARBluejay | 0.0403
ACAR | Bluejay | 1198 | 24/13 | 1.259 | 0.0152 | 0.0159 | 0.01735 | 0.0188 | 0.462 | 0.0738 |  | ACARBluejay | 0.0403
ACAR | Bunting | 1277 | 54/7 | 1.302 | 0.0138 | 0.0149 | 0.01615 | 0.0174 | 0.456 | 0.0729 |  | ACARBunting | 0.0419
ACAR | Bunting | 1277 | 42/19 | 1.302 | 0.0142 | 0.0152 | 0.0165 | 0.0178 | 0.456 | 0.0729 |  | ACARBunting | 0.0419
ACAR | Bittern | 1361.5 | 54/7 | 1.345 | 0.0129 | 0.0138 | 0.01505 | 0.0163 | 0.451 | 0.0721 |  | ACARBittern | 0.0433
ACAR | Bobolink | 1534.4 | 42/19 | 1.427 | 0.0118 | 0.0127 | 0.01395 | 0.0152 | 0.442 | 0.0708 | 1314 | ACARBobolink | 0.0459
ACAR | Lapwing | 1703 | 48/13 | 1.504 | 0.0105 | 0.0115 | 0.0125 | 0.0135 | 0.434 | 0.0696 |  | ACARLapwing | 0.0484
ACAR | Falcon | 1798 | 42/19 | 1.545 | 0.0101 | 0.011 | 0.0119 | 0.0128 | 0.43 | 0.069 |  | ACARFalcon | 0.0497
ACAR | Chukar | 1933 | 42/19 | 1.602 | 0.0094 | 0.0102 | 0.0112 | 0.0122 | 0.424 | 0.0682 | 1465 | ACARChukar | 0.0515
ACAR | Bluebird | 2338 | 42/19 | 1.762 | 0.0078 | 0.0089 | 0.0096 | 0.0103 | 0.409 | 0.066 |  | ACARBluebird | 0.0567
ACAR | Bluebird | 2338 | 48/13 | 1.762 | 0.0077 | 0.0088 | 0.0095 | 0.0102 | 0.409 | 0.066 |  | ACARBluebird | 0.0567
ACAR | Kingfisher | 2493 | 54/37 | 1.821 | 0.0074 | 0.0087 | 0.00935 | 0.01 | 0.404 | 0.0652 | 1670 | ACARKingfisher | 0.0587
ACCC | OCEANSIDE | 383.2 |  | 0.68 | 0.04392 | 0.044962 |  |  | 0.020019 | 0.086591 | 558 | ACCCOCEANSIDE
ACCC | LINNET | 430.5 |  | 0.72 | 0.03892 | 0.03983 |  |  | 0.019697 | 0.085341 | 602 | ACCCLINNET
ACCC | ORIOLE | 438.6 |  | 0.741 | 0.038239 | 0.03911 |  |  | 0.019545 | 0.084413 | 612 | ACCCORIOLE
ACCC | WACO | 454 |  | 0.77 | 0.036951 | 0.037803 |  |  | 0.019318 | 0.083428 | 628 | ACCCWACO
ACCC | LAREDO | 529.8 |  | 0.807 | 0.031648 | 0.032424 |  |  | 0.019053 | 0.08267 | 687 | ACCCLAREDO
ACCC | IRVING | 609.5 |  | 0.882 | 0.027538 | 0.028239 |  |  | 0.018561 | 0.08036 | 753 | ACCCIRVING
ACCC | HAWK | 611.3 |  | 0.858 | 0.027424 | 0.028125 |  |  | 0.018712 | 0.081364 | 753 | ACCCHAWK
ACCC | DOVE | 713.5 |  | 0.927 | 0.023485 | 0.024129 |  |  | 0.018277 | 0.079545 | 826 | ACCCDOVE
ACCC | AMARILLO | 784.7 |  | 0.99 | 0.021439 | 0.022121 |  |  | 0.017917 | 0.077784 | 879 | ACCCAMARILLO
ACCC | GROSBEAK | 821.4 |  | 0.99 | 0.020473 | 0.021098 |  |  | 0.017917 | 0.078049 | 898 | ACCCGROSBEAK
ACCC | LUBBOCK | 903.9 |  | 1.04 | 0.018542 | 0.019148 |  |  | 0.017633 | 0.076913 | 956 | ACCCLUBBOCK
ACCC | GALVESTON | 1011.3 |  | 1.09 | 0.016572 | 0.017178 |  |  | 0.017367 | 0.07589 | 1022 | ACCCGALVESTON
ACCC | DRAKE | 1025.6 |  | 1.108 | 0.016345 | 0.016894 |  |  | 0.017273 | 0.075398 | 1036 | ACCCDRAKE
ACCC | CURLEW | 1033 |  | 1.14 | 0.016326 | 0.017008 |  |  | 0.017121 | 0.074621 | 1042 | ACCCCURLEW
ACCC | PLANO | 1059.5 |  | 1.127 | 0.015909 | 0.016591 |  |  | 0.017178 | 0.075208 | 1050 | ACCCPLANO
ACCC | CORPUS_CHRISTI | 1103 |  | 1.146 | 0.015265 | 0.015966 |  |  | 0.017083 | 0.074848 | 1076 | ACCCCORPUS_CHRISTI
ACCC | ARLINGTON | 1151 |  | 1.177 | 0.01464 | 0.015322 |  |  | 0.016932 | 0.074148 | 1106 | ACCCARLINGTON
ACCC | CARDINAL | 1221.8 |  | 1.198 | 0.013788 | 0.014432 |  |  | 0.016837 | 0.073864 | 1146 | ACCCCARDINAL
ACCC | FORT_WORTH | 1300.4 |  | 1.24 | 0.012955 | 0.013655 |  |  | 0.016648 | 0.073011 | 1189 | ACCCFORT_WORTH
ACCC | EL_PASO | 1349.9 |  | 1.252 | 0.012481 | 0.01322 |  |  | 0.016591 | 0.072917 | 1212 | ACCCEL_PASO
ACCC | BEAUMONT | 1428.6 |  | 1.294 | 0.011799 | 0.012519 |  |  | 0.016402 | 0.072102 | 1257 | ACCCBEAUMONT
ACCC | SAN_ANTONIO | 1474.9 |  | 1.315 | 0.01142 | 0.011799 |  |  | 0.016307 | 0.071723 | 1302 | ACCCSAN_ANTONIO
ACCC | BITTERN | 1581.6 |  | 1.345 | 0.01072 | 0.01142 |  |  | 0.016193 | 0.071364 | 1331 | ACCCBITTERN
ACCC | DALLAS | 1794.9 |  | 1.452 | 0.0094129 | 0.010341 |  |  | 0.015758 | 0.069545 | 1434 | ACCCDALLAS
ACCC | HOUSTON | 1927.4 |  | 1.506 | 0.0086932 | 0.0096591 |  |  | 0.015549 | 0.068655 | 1502 | ACCCHOUSTON
ACCC | LAPWING | 1948.9 |  | 1.504 | 0.0086742 | 0.0096023 |  |  | 0.015568 | 0.068807 | 1502 | ACCCLAPWING
ACCC | FALCON | 2045.1 |  | 1.545 | 0.0082576 | 0.009072 |  |  | 0.015417 | 0.068125 | 1555 | ACCCFALCON
ACCC | BLUEBIRD | 2740.6 |  | 1.762 | 0.0061742 | 0.0073295 |  |  | 0.014678 | 0.065246 | 1808 | ACCCBLUEBIRD

## Validation
VALIDATIONS
Structure type | conductor_type
Lattice | AAC
Pole | ACSR
H Frame | AAAC
Y | ACAR

## Sources
Sources
Insulators string distance:IEC 60071-2 Insulation co-ordination application guite part 2 (creepage distance). AND IEC 60305 IEC Insulators classes
EPRI Transmission reference book
Stevenson, Grainger
| typical bundling | Oregon state U | Section 4 Transmission Lines.pdf (oregonstate.edu)

## TL_Geometry (2)
code | structure_type | company | state | n_circuits | n_ground_w | voltage_kv | Creep_Dist_mm_kv | Insul_Creep_Dist_mm | Insul_Spac_mm | L_Ins_String_ft | ha1t_ft | hb1t_ft | hc1t_ft | Sa1t_ft | Sb1t_ft | Sc1t_ft | hg11t_ft | Sg11t_ft | hg21t_ft | Sg21t_ft | ha2t_ft | hb2t_ft | hc2t_ft | Sa2t_ft | Sb2t_ft | Sc2t_ft | ha1 (ft) | ha1 (inch) | hb1 (ft) | hb1 (inch) | hc1 (ft) | hc1 (inch) | Sa1 (ft) | Sa1 (inch) | Sb1 (ft) | Sb1 (inch) | Sc1 (ft) | Sc1 (inch) | hg11 (ft) | hg11 (inch) | Sg11 (ft) | Sg11 (inch) | hg21 (ft) | hg21 (inch) | Sg21 (ft) | Sg21 (inch) | ha2 (ft) | ha2 (inch) | hb2 (ft) | hb2 (inch) | hc2 (ft) | hc2 (inch) | Sa2 (ft) | Sa2 (inch) | Sb2 (ft) | Sb2 (inch) | Sc2 (ft) | Sc2 (inch)
3L1 | Lattice | Iowa Public Service Co | Iowa | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -23.75 | 0 | 23.75 | 87.5 | -17.8125 | 87.5 | 17.8125 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -23 | -9 | 0 | 0 | 23 | 9 | 87 | 6 | -17.25 | -6.75 | 87 | 6 | 17.25 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L2 | Lattice | Indianapolis Power and Light Company, Western Power Area Administration | Indiana, Colorado | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -32 | 0 | 32 | 96.5 | -21.5 | 96.5 | 21.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -32 | 0 | 0 | 0 | 32 | 0 | 96 | 6 | -21 | -6 | 96 | 6 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L3 | Lattice | Consumers Power Company | Michigan | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 59.1594 | 59.1594 | -24.5 | 0 | 24.5 | 87.5 | -16.5 | 87.5 | 16.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | -24 | -6 | 0 | 0 | 24 | 6 | 87 | 6 | -16 | -6 | 87 | 6 | 16 | 6
3L4 | Lattice | Pennsylvania Electric Co | Pensylvania | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.1594 | 44.1594 | 44.1594 | -22.6667 | 0 | 22.6667 | 73 | -18.5833 | 73 | 18.5833 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 0 | 55 | 0 | 55 | 0 | -22 | -8 | 0 | 0 | 22 | 8 | 73 | 0 | -18 | -7 | 73 | 0 | 18 | 7
3L5 | Lattice | Northern Indiana Public Service | Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 79.1594 | 79.1594 | 79.1594 | -24 | 0 | 24 | 102 | -21.6 | 102 | 21.6 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 90 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 102 | 0 | -21.6 | 0 | 102 | 0 | 21.6 | 0
3L6 | Lattice | Cleveland electric iluminating | Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 43.6594 | 43.6594 | 43.6594 | -23 | 0 | 23 | 94.5 | -20.5 | 94.5 | 20.5 | 72.1594 | 72.1594 | 72.1594 | 23 | 0 | -23 | 54 | 6 | 54 | 6 | 54 | 6 | -23 | 0 | 0 | 0 | 23 | 0 | 93 | 18 | -20 | -6 | 93 | 18 | 20 | 6 | 82 | 12 | 82 | 12 | 82 | 12 | 23 | 0 | 0 | 0 | -23 | 0
3L7 | Lattice | Consolidated Edison Co | New York | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 41.826 | 64.826 | 87.826 | -19 | -17.5 | -15.3333 | 104.6667 | -12 | 104.6667 | 12 | 87.826 | 64.826 | 41.826 | 15.3333 | 17.5 | 19 | 52 | 8 | 75 | 8 | 98 | 8 | -19 | 0 | -17 | -6 | -15 | -4 | 104 | 8 | -12 | 0 | 104 | 8 | 12 | 0 | 98 | 8 | 75 | 8 | 52 | 8 | 15 | 4 | 17 | 6 | 19 | 0
3L8 | Lattice | Oklahoma Gas & Electric Co, American Electric Power Co | Oklahoma, Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 93.1594 | 117.1594 | -22 | -37 | -22 | 142 | -11 | 142 | 11 | 117.1594 | 93.1594 | 69.1594 | 22 | 37 | 22 | 80 | 0 | 104 | 0 | 128 | 0 | -22 | 0 | -37 | 0 | -22 | 0 | 142 | 0 | -11 | 0 | 142 | 0 | 11 | 0 | 128 | 0 | 104 | 0 | 80 | 0 | 22 | 0 | 37 | 0 | 22 | 0
3L9 | Lattice | Consumers Power Company, Indianapolis Power and Light Company | Michigan, Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 89.1594 | 111.1594 | -18 | -29 | -17 | 137 | -24 | 137 | 24 | 111.1594 | 89.1594 | 69.1594 | 17 | 29 | 18 | 80 | 0 | 100 | 0 | 122 | 0 | -18 | 0 | -29 | 0 | -17 | 0 | 137 | 0 | -24 | 0 | 137 | 0 | 24 | 0 | 122 | 0 | 100 | 0 | 80 | 0 | 17 | 0 | 29 | 0 | 18 | 0
3L10 | Lattice | Detroit Edison | Michigan | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 53.1594 | 74.6594 | 98.6594 | -20.5 | -27 | -18.5 | 119.5 | -25.75 | 119.5 | 25.75 | 98.6594 | 74.6594 | 53.1594 | 18.5 | 27 | 20.5 | 64 | 0 | 85 | 6 | 109 | 6 | -20 | -6 | -27 | 0 | -18 | -6 | 119 | 6 | -25 | -9 | 119 | 6 | 25 | 9 | 109 | 6 | 85 | 6 | 64 | 0 | 18 | 6 | 27 | 0 | 20 | 6
3L13 | Lattice | Union electric company | Missouri, Nebraska, Minnesota | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 91.1594 | 65.1594 | 65.1594 | -17.6667 | -37 | -17 | 109 | -23.3333 | 109 | 23.3333 | 91.1594 | 65.1594 | 65.1594 | 17.6667 | 17 | 37 | 102 | 0 | 76 | 0 | 76 | 0 | -17 | -8 | -37 | 0 | -17 | 0 | 109 | 0 | -23 | -4 | 109 | 0 | 23 | 4 | 102 | 0 | 76 | 0 | 76 | 0 | 17 | 8 | 17 | 0 | 37 | 0
3L14 | Lattice | Texas electric service & Light Co | Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 77.1594 | 52.1594 | 52.1594 | -25.5833 | -37.8333 | -14.3333 | 103 | -15.6667 | 103 | 15.6667 | 77.1594 | 52.1594 | 52.1594 | 25.5833 | 14.3333 | 37.8333 | 88 | 0 | 63 | 0 | 63 | 0 | -25 | -7 | -37 | -10 | -14 | -4 | 103 | 0 | -15 | -8 | 103 | 0 | 15 | 8 | 88 | 0 | 63 | 0 | 63 | 0 | 25 | 7 | 14 | 4 | 37 | 10
3L15 | Lattice | Commonwealth Edison Company | Chicago | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 97.1594 | 54.1594 | 54.1594 | -28.5 | -40.5 | -16.5 | 117 | -40.5 | 117 | 40.5 | 97.1594 | 54.1594 | 54.1594 | 69 | 16.5 | 81 | 108 | 0 | 65 | 0 | 65 | 0 | -28.5 | 0 | -40.5 | 0 | -16.5 | 0 | 117 | 0 | -40.5 | 0 | 117 | 0 | 40.5 | 0 | 108 | 0 | 65 | 0 | 65 | 0 | 69 | 0 | 16.5 | 0 | 81 | 0
3P1 | Pole | Dayton Power & Light company | Ohio | 1 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 64.1594 | 75.6594 | 87.1594 | 9 | -9 | 9 | 131.5 | 0 | 0 | 0 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 75 | 0 | 86 | 6 | 98 | 0 | 9 | 0 | -9 | 0 | 9 | 0 | 131 | 6 | 0 | 0 | 0 | 0 | 0 | 0
3P2 | Pole | Cleveland electric iluminating, Indianapolis Power and Light Company, Northeast Utilities | Ohio, Indiana, New Hampshire, Massachusets, Connecticut | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 54.1594 | 77.1594 | 100.1594 | -15 | -15 | -15 | 132 | -14 | 132 | 14 | 100.1594 | 77.1594 | 54.1594 | 15 | 15 | 15 | 65 | 0 | 88 | 0 | 111 | 0 | -15 | 0 | -15 | 0 | -15 | 0 | 132 | 0 | -14 | 0 | 132 | 0 | 14 | 0 | 111 | 0 | 88 | 0 | 65 | 0 | 15 | 0 | 15 | 0 | 15 | 0
3P3 | Pole | Northern States Power Company, Wisconsin Electric Power Co | Minnesota, Wisconsin | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 90.1594 | 115.1594 | -14.25 | -21.25 | -14.25 | 135 | -17 | 135 | 17 | 115.1594 | 90.1594 | 65.1594 | 14.25 | 21.25 | 14.25 | 76 | 0 | 101 | 0 | 126 | 0 | -14 | -3 | -21 | -3 | -14 | -3 | 135 | 0 | -17 | 0 | 135 | 0 | 17 | 0 | 126 | 0 | 101 | 0 | 76 | 0 | 14 | 3 | 21 | 3 | 14 | 3
3P4 | Pole | Consolidated Edison Co, Houston Lightning Company, SouthWestern electric company | New York, Texas, Arkansas, Lousiana, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 81.1594 | 97.1594 | -11 | -11 | -11 | 111.5 | -8 | 111.5 | 8 | 97.1594 | 81.1594 | 65.1594 | 11 | 11 | 11 | 76 | 0 | 92 | 0 | 108 | 0 | -11 | 0 | -11 | 0 | -11 | 0 | 111 | 6 | -8 | 0 | 111 | 6 | 8 | 0 | 108 | 0 | 92 | 0 | 76 | 0 | 11 | 0 | 11 | 0 | 11 | 0
3P5 | Pole | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 72 | 97 | 122 | -11 | -19 | -11 | 140 | -7 | 140 | 7 | 122 | 97 | 72 | 11 | 19 | 11 | 82.8406 | 0 | 107.8406 | 0 | 132.8406 | 0 | -11 | 0 | -19 | 0 | -11 | 0 | 140 | 0 | -7 | 0 | 140 | 0 | 7 | 0 | 132.8406 | 0 | 107.8406 | 0 | 82.8406 | 0 | 11 | 0 | 19 | 0 | 11 | 0
3P6 | Pole | Dayton Power & Light company | Ohio | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 81.6594 | 104.1594 | -9 | -13 | -9 | 145.5 | 0 | 0 | 0 | 104.1594 | 81.6594 | 59.1594 | -9 | -13 | -9 | 70 | 0 | 92 | 6 | 114 | 12 | -9 | 0 | -13 | 0 | -9 | 0 | 144 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 12 | 92 | 6 | 70 | 0 | -9 | 0 | -13 | 0 | -9 | 0
3P7 | Pole | Illinois Power Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.826 | 80.826 | 80.826 | -15.5 | -41 | -16 | 127.6667 | -30 | 127.6667 | 30 | 116.826 | 80.826 | 80.826 | 15.5 | 16 | 41 | 127 | 8 | 91 | 8 | 91 | 8 | -15 | -6 | -41 | 0 | -16 | 0 | 127 | 8 | -30 | 0 | 127 | 8 | 30 | 0 | 127 | 8 | 91 | 8 | 91 | 8 | 15 | 6 | 16 | 0 | 41 | 0
3P8 | Pole | Commonwealth Edison Company | Chicago | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 98.1594 | 55.1594 | 55.1594 | -22 | -33 | -10 | 118 | 0 | 0 | 0 | 98.1594 | 55.1594 | 55.1594 | 22 | 10 | 33 | 109 | 0 | 66 | 0 | 66 | 0 | -22 | 0 | -33 | 0 | -10 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 66 | 0 | 66 | 0 | 22 | 0 | 10 | 0 | 33 | 0
3H1 | H frame | Public Service Company of New Hampshire | New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -18 | 0 | 18 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -18 | 0 | 0 | 0 | 18 | 0 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H2 | H frame | Utah Power and Light Company | Utah | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 62.1594 | 62.1594 | 62.1594 | -27 | 0 | 27 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 73 | 0 | 73 | 0 | 73 | 0 | -26 | -12 | 0 | 0 | 26 | 12 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H3 | H frame | Niagara Mohawk Power Corporation, Illinois Power Company, Central Maine Power Co | New York, Illinois, Maine, New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.826 | 44.826 | 44.826 | -26 | 0 | 26 | 65.5 | -13 | 65.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 8 | 55 | 8 | 55 | 8 | -26 | 0 | 0 | 0 | 26 | 0 | 64 | 18 | -13 | 0 | 64 | 18 | 13 | 0
3H4 | H frame | Public Service Company of New Hampshire, Northeast Utilities, New York State Electric & Gas, Vermont Electric Company, Wisconsin Public Service Corp | New Hampshire, Massachusets, Connecticut, New York, Vermont, Wisconsin | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 50.1594 | 50.1594 | 50.1594 | -26 | 0 | 26 | 73.5 | -13 | 73.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 61 | 0 | 61 | 0 | 61 | 0 | -26 | 0 | 0 | 0 | 26 | 0 | 73.5 | 0 | -13 | 0 | 73.5 | 0 | 13 | 0
3H5 | H frame | El paso electric company | Texas, New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 59.1594 | 52.6594 | -27 | 0 | 27 | 78 | -13.5 | 78 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 69 | 12 | 63 | 6 | -26 | -12 | 0 | 0 | 26 | 12 | 77 | 12 | -13.5 | 0 | 77 | 12 | 13.5 | 0
3H6 | H frame | Northern States Power Company, Wisconsin Electric Power Co, Kansas Gas & Electric Co | Minnesota, Wisconsin, Kansas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 46.6594 | 58.1594 | 46.6594 | -28.25 | 0 | 28.25 | 69 | -15.25 | 69 | 15.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 57 | 6 | 68 | 12 | 57 | 6 | -28 | -3 | 0 | 0 | 28 | 3 | 68 | 12 | -15 | -3 | 68 | 12 | 15 | 3
3H7 | H frame | Public Service Company of New Mexico | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -23.5 | 0 | 23.5 | 68.5 | -13.5 | 68.5 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -23 | -6 | 0 | 0 | 23 | 6 | 68 | 6 | -13.5 | 0 | 68 | 6 | 13.5 | 0
3H8 | H frame | Union electric company | Missouri, Nebraska, Minnesota | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 51.1594 | 51.1594 | 51.1594 | -24 | 0 | 24 | 72.5 | -26 | 72.5 | 26 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 62 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 72 | 6 | -26 | 0 | 72 | 6 | 26 | 0
3H9 | H frame | New Englad Electric System | New Englad, New Hampshire, Massachusets | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 52.6594 | 52.6594 | -20 | 0 | 20 | 74.5 | -9.5 | 74.5 | 9.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 63 | 6 | 63 | 6 | -19 | -12 | 0 | 0 | 19 | 12 | 74 | 6 | -9 | -6 | 74 | 6 | 9 | 6
3H10 | H frame | Boston Edison Company | Massachusets | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 96 | 70 | 70 | -10 | -32.75 | -10 | 111 | -27.25 | 111 | 27.25 | 96 | 70 | 70 | 10 | 10 | 32.75 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | -10 | 0 | -32 | -9 | -10 | 0 | 111 | 0 | -27 | -3 | 111 | 0 | 27 | 3 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | 10 | 0 | 10 | 0 | 32 | 9
3Y1 | Y | Tucson Gas & Electric Co | Arizona | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 109.2427 | 84.6594 | 84.6594 | 0 | -15 | 15 | 120.0833 | -13.5 | 120.0833 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 119 | 13 | 95 | 6 | 95 | 6 | 0 | 0 | -15 | 0 | 15 | 0 | 119 | 13 | -13.5 | 0 | 119 | 13 | 13.5 | 0
3Y2 | Y | Pacific Power Light corp |  | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -13.5 | 13.5 | 127 | -10 | 127 | 10 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -13 | -6 | 13 | 6 | 127 | 0 | -10 | 0 | 127 | 0 | 10 | 0
3Y3 | Y | SouthWestern electric company | Arkansas, Lousiana, Texas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -19.8333 | 19.8333 | 127 | -9 | 127 | 9 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -19.5 | -4 | 19.5 | 4 | 127 | 0 | -9 | 0 | 127 | 0 | 9 | 0
5L1 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 96.7889 | 69.2889 | 69.2889 | 0 | -20 | 20 | 122.25 | -13 | 122.25 | 13 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 112 | 6 | 85 | 0 | 85 | 0 | 0 | 0 | -20 | 0 | 20 | 0 | 121 | 15 | -13 | 0 | 121 | 15 | 13 | 0
5L2 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 98.2889 | 69.2889 | 69.2889 | 0 | -15.3333 | 15.3333 | 121 | -12 | 121 | 12 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 114 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -15 | -4 | 15 | 4 | 121 | 0 | -12 | 0 | 121 | 0 | 12 | 0
5L3 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 90.2889 | 74.2889 | 74.2889 | 0 | -29 | 29 | 106 | -15 | 106 | 15 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 106 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | -29 | 0 | 29 | 0 | 106 | 0 | -15 | 0 | 106 | 0 | 15 | 0
5L4 | Lattice | Basin Electric Power Co-op | California, North Dakota, South Dakota, Colorado, Montana, New Mexico, Wyoming, Minnesota, Iowa | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 85 | 69.2889 | 69.2889 | 0 | -28 | 28 | 99 | -26 | 99 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 100.7111 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -28 | 0 | 28 | 0 | 99 | 0 | -26 | 0 | 99 | 0 | 26 | 0
5L5 | Lattice | Carolina Power & Light Co | North Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 105 | 89.2889 | 89.2889 | 0 | -30.25 | 30.25 | 122.5 | -15.5 | 122.5 | 15.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120.7111 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -30 | -3 | 30 | 3 | 122 | 6 | -15.5 | 0 | 122 | 6 | 15.5 | 0
5L6 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 64.2889 | 64.2889 | 64.2889 | 0 | -35 | 35 | 95 | -25 | 95 | 25 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 95 | 0 | -25 | 0 | 95 | 0 | 25 | 0
5L7 | Lattice | Alabama Power Company, Baltimore Gas and Electric Company | Alabama, Maryland, | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -34 | 34 | 124 | -31 | 124 | 31 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -34 | 0 | 34 | 0 | 124 | 0 | -31 | 0 | 124 | 0 | 31 | 0
5L8 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -33 | 33 | 129 | -20 | 129 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -33 | 0 | 33 | 0 | 129 | 0 | -20 | 0 | 129 | 0 | 20 | 0
5L9 | Lattice | American Electric Power Co, Arizona Public Service Co, Duke Power Company | Virginia, Arizona, South Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 79.2889 | 79.2889 | 79.2889 | 0 | -32 | 32 | 109 | -24 | 109 | 24 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 0 | 0 | -32 | 0 | 32 | 0 | 109 | 0 | -24 | 0 | 109 | 0 | 24 | 0
5L10 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -35 | 35 | 137 | -26 | 137 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 137 | 0 | -26 | 0 | 137 | 0 | 26 | 0
5L11 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 100.2889 | 131.2889 | -15 | -25 | -15 | 172 | 0 | 0 | 0 | 131.2889 | 100.2889 | 69.2889 | 15 | 25 | 15 | 85 | 0 | 116 | 0 | 147 | 0 | -15 | 0 | -25 | 0 | -15 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 116 | 0 | 85 | 0 | 15 | 0 | 25 | 0 | 15 | 0
5L12 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 114.2889 | 69.2889 | 69.2889 | -27.75 | -40.5 | -15 | 150 | -18.5 | 150 | 18.5 | 114.2889 | 69.2889 | 69.2889 | 27.75 | 15 | 40.5 | 130 | 0 | 85 | 0 | 85 | 0 | -27 | -9 | -40 | -6 | -15 | 0 | 150 | 0 | -18.5 | 0 | 150 | 0 | 18.5 | 0 | 130 | 0 | 85 | 0 | 85 | 0 | 27 | 9 | 15 | 0 | 40 | 6
5L13 | Lattice |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 112.2889 | 74.2889 | 74.2889 | -18.5 | -46.5 | -18.5 | 140 | -12.125 | 140 | 15.125 | 112.2889 | 74.2889 | 74.2889 | 18.5 | 18.5 | 46.5 | 128 | 0 | 90 | 0 | 90 | 0 | -18 | -6 | -46 | -6 | -18 | -6 | 140 | 0 | -12 | -1.5 | 140 | 0 | 15 | 1.5 | 128 | 0 | 90 | 0 | 90 | 0 | 18 | 6 | 18 | 6 | 46 | 6
5L14 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | -42 | 0 | 42 | 128 | -21.8333 | 128 | 21.8333 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -42 | 0 | 0 | 0 | 42 | 0 | 128 | 0 | -21 | -10 | 128 | 0 | 21 | 10
5P1 | Pole |  |  | 1 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 99.2889 | 129.2889 | 18 | 21 | 18 | 160 | 4 | 0 | 0 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 85 | 0 | 115 | 0 | 145 | 0 | 18 | 0 | 21 | 0 | 18 | 0 | 160 | 0 | 4 | 0 | 0 | 0 | 0 | 0
5P2 | Pole |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 60.7056 | 73.2889 | 85.7056 | 18 | -17 | 18 | 120 | -10 | 120 | 10 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 77 | -7 | 90 | -12 | 102 | -7 | 18 | 0 | -17 | 0 | 18 | 0 | 120 | 0 | -10 | 0 | 120 | 0 | 10 | 0
5H1 | H frame | Baltimore Gas and Electric Company, Baltimore Gas and Electric Company | Maryland, Maryland | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 104.2889 | 104.2889 | 104.2889 | -35 | 0 | 35 | 129 | -26 | 129 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | -35 | 0 | 0 | 0 | 35 | 0 | 129 | 0 | -26 | 0 | 129 | 0 | 26 | 0
5H2 | H frame |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 123 | 87 | 87 | -30 | -45 | -15 | 149 | -32 | 149 | 32 | 123 | 87 | 87 | 15 | 45 | 15 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | -30 | 0 | -45 | 0 | -15 | 0 | 149 | 0 | -32 | 0 | 149 | 0 | 32 | 0 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | 15 | 0 | 45 | 0 | 15 | 0
5Y1 | Y |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 106.25 | 139.25 | 106.25 | -21.5 | 0 | 21.5 | 153 | -13.75 | 153 | 13.75 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 122.7111 | -9 | 155.7111 | -9 | 122.7111 | -9 | -21 | -6 | 0 | 0 | 21 | 6 | 153 | 0 | -13 | -9 | 153 | 0 | 13 | 9
5Y2 | Y | Arkansas Power & Light Co. | Arkansas | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 118.5 | 88 | 88 | 0 | -21.5 | 21.5 | 131.5 | -20 | 131.5 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 133.7111 | 6 | 103.7111 | 0 | 103.7111 | 0 | 0 | 0 | -21 | -6 | 21 | 6 | 131 | 6 | -20 | 0 | 131 | 6 | 20 | 0
5Y3 | Y | Alabama Power Company | Alabama | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 151.25 | 126 | 126 | 0 | -21 | 21 | 165.25 | -17.5 | 165.25 | 17.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 166.7111 | 3 | 141.7111 | 0 | 141.7111 | 0 | 0 | 0 | -21 | 0 | 21 | 0 | 165 | 3 | -17 | -6 | 165 | 3 | 17 | 6
7L1 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 92 | 92 | 92 | -44.5 | 0 | 44.5 | 127 | -36 | 127 | 36 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 115.0953 | 0 | 115.0953 | 0 | 115.0953 | 0 | -44 | -6 | 0 | 0 | 44 | 6 | 127 | 0 | -36 | 0 | 127 | 0 | 36 | 0
7L2 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 86.9047 | 86.9047 | 86.9047 | -45 | 0 | 45 | 138.6667 | -50 | 138.6667 | 50 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -45 | 0 | 0 | 0 | 45 | 0 | 138 | 8 | -50 | 0 | 138 | 8 | 50 | 0
7L3 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 135 | 135 | 135 | -41.8333 | 0 | 41.8333 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 158.0953 | 0 | 158.0953 | 0 | 158.0953 | 0 | -41 | -10 | 0 | 0 | 41 | 10 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7P1 | Pole |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 100.9047 | 100.9047 | 100.9047 | -39.3333 | 0 | 39.3333 | 145 | -66 | 145 | 66 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 124 | 0 | 124 | 0 | 124 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 145 | 0 | -66 | 0 | 145 | 0 | 66 | 0
7H1 | H frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 131 | 131 | 131 | -50 | 0 | 50 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 154.0953 | 0 | 154.0953 | 0 | 154.0953 | 0 | -50 | 0 | 0 | 0 | 50 | 0 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7V1 | V frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 110 | 110 | 110 | -39.3333 | 0 | 39.3333 | 150 | -30 | 150 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 133.0953 | 0 | 133.0953 | 0 | 133.0953 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 150 | 0 | -30 | 0 | 150 | 0 | 30 | 0
DC1 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0
DC2 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0