## TL_Geometry
code | structure_type | company | state | n_circuits | n_ground_w | voltage_kv | Creep_Dist_mm_kv | Insul_Creep_Dist_mm | Insul_Spac_mm | L_Ins_String_ft | ha1t_ft | hb1t_ft | hc1t_ft | Sa1t_ft | Sb1t_ft | Sc1t_ft | hg11t_ft | Sg11t_ft | hg21t_ft | Sg21t_ft | ha2t_ft | hb2t_ft | hc2t_ft | Sa2t_ft | Sb2t_ft | Sc2t_ft | ha1 (ft) | ha1 (inch) | hb1 (ft) | hb1 (inch) | hc1 (ft) | hc1 (inch) | Sa1 (ft) | Sa1 (inch) | Sb1 (ft) | Sb1 (inch) | Sc1 (ft) | Sc1 (inch) | hg11 (ft) | hg11 (inch) | Sg11 (ft) | Sg11 (inch) | hg21 (ft) | hg21 (inch) | Sg21 (ft) | Sg21 (inch) | ha2 (ft) | ha2 (inch) | hb2 (ft) | hb2 (inch) | hc2 (ft) | hc2 (inch) | Sa2 (ft) | Sa2 (inch) | Sb2 (ft) | Sb2 (inch) | Sc2 (ft) | Sc2 (inch)
3L1 | Lattice | Iowa Public Service Co | Iowa | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -23.75 | 0 | 23.75 | 87.5 | -17.8125 | 87.5 | 17.8125 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -23 | -9 | 0 | 0 | 23 | 9 | 87 | 6 | -17.25 | -6.75 | 87 | 6 | 17.25 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L2 | Lattice | Indianapolis Power and Light Company, Western Power Area Administration | Indiana, Colorado | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -32 | 0 | 32 | 96.5 | -21.5 | 96.5 | 21.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -32 | 0 | 0 | 0 | 32 | 0 | 96 | 6 | -21 | -6 | 96 | 6 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L3 | Lattice | Consumers Power Company | Michigan | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 59.1594 | 59.1594 | -24.5 | 0 | 24.5 | 87.5 | -16.5 | 87.5 | 16.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | -24 | -6 | 0 | 0 | 24 | 6 | 87 | 6 | -16 | -6 | 87 | 6 | 16 | 6
3L4 | Lattice | Pennsylvania Electric Co | Pensylvania | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.1594 | 44.1594 | 44.1594 | -22.6667 | 0 | 22.6667 | 73 | -18.5833 | 73 | 18.5833 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 0 | 55 | 0 | 55 | 0 | -22 | -8 | 0 | 0 | 22 | 8 | 73 | 0 | -18 | -7 | 73 | 0 | 18 | 7
3L5 | Lattice | Northern Indiana Public Service | Indiana | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 79.1594 | 79.1594 | 79.1594 | -24 | 0 | 24 | 102 | -21.6 | 102 | 21.6 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 90 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 102 | 0 | -21.6 | 0 | 102 | 0 | 21.6 | 0
3L6 | Lattice | Cleveland electric iluminating | Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 43.6594 | 43.6594 | 43.6594 | -23 | 0 | 23 | 94.5 | -20.5 | 94.5 | 20.5 | 72.1594 | 72.1594 | 72.1594 | 23 | 0 | -23 | 54 | 6 | 54 | 6 | 54 | 6 | -23 | 0 | 0 | 0 | 23 | 0 | 93 | 18 | -20 | -6 | 93 | 18 | 20 | 6 | 82 | 12 | 82 | 12 | 82 | 12 | 23 | 0 | 0 | 0 | -23 | 0
3L7 | Lattice | Consolidated Edison Co | New York | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 41.826 | 64.826 | 87.826 | -19 | -17.5 | -15.3333 | 104.6667 | -12 | 104.6667 | 12 | 87.826 | 64.826 | 41.826 | 15.3333 | 17.5 | 19 | 52 | 8 | 75 | 8 | 98 | 8 | -19 | 0 | -17 | -6 | -15 | -4 | 104 | 8 | -12 | 0 | 104 | 8 | 12 | 0 | 98 | 8 | 75 | 8 | 52 | 8 | 15 | 4 | 17 | 6 | 19 | 0
3L8 | Lattice | Oklahoma Gas & Electric Co, American Electric Power Co | Michigan, Oklahoma, Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 93.1594 | 117.1594 | -22 | -37 | -22 | 142 | -11 | 142 | 11 | 117.1594 | 93.1594 | 69.1594 | 22 | 37 | 22 | 80 | 0 | 104 | 0 | 128 | 0 | -22 | 0 | -37 | 0 | -22 | 0 | 142 | 0 | -11 | 0 | 142 | 0 | 11 | 0 | 128 | 0 | 104 | 0 | 80 | 0 | 22 | 0 | 37 | 0 | 22 | 0
3L9 | Lattice | Consumers Power Company, Indianapolis Power and Light Company | Michigan, Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 89.1594 | 111.1594 | -18 | -29 | -17 | 137 | -24 | 137 | 24 | 111.1594 | 89.1594 | 69.1594 | 17 | 29 | 18 | 80 | 0 | 100 | 0 | 122 | 0 | -18 | 0 | -29 | 0 | -17 | 0 | 137 | 0 | -24 | 0 | 137 | 0 | 24 | 0 | 122 | 0 | 100 | 0 | 80 | 0 | 17 | 0 | 29 | 0 | 18 | 0
3L10 | Lattice | Detroit Edison | Michigan | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 53.1594 | 74.6594 | 98.6594 | -20.5 | -27 | -18.5 | 119.5 | -25.75 | 119.5 | 25.75 | 98.6594 | 74.6594 | 53.1594 | 18.5 | 27 | 20.5 | 64 | 0 | 85 | 6 | 109 | 6 | -20 | -6 | -27 | 0 | -18 | -6 | 119 | 6 | -25 | -9 | 119 | 6 | 25 | 9 | 109 | 6 | 85 | 6 | 64 | 0 | 18 | 6 | 27 | 0 | 20 | 6
3L11 | Lattice | Boston Edison Company, Consolidated Edison Co of New York, Houston Lightning Company | Massachusets, New York, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 39.1594 | 61.1594 | 83.1594 | -25 | -25 | -25 | 98.5 | -18 | 98.5 | 18 | 83.1594 | 61.1594 | 39.1594 | -25 | -25 | -25 | 50 | 0 | 72 | 0 | 94 | 0 | -25 | 0 | -25 | 0 | -25 | 0 | 98 | 6 | -18 | 0 | 98 | 6 | 18 | 0 | 94 | 0 | 72 | 0 | 50 | 0 | -25 | 0 | -25 | 0 | -25 | 0
3L12 | Lattice | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 61.6594 | 89.6594 | 117.6594 | -15 | -20 | -15 | 136 | -9 | 136 | 9 | 117.6594 | 89.6594 | 61.6594 | 15 | 20 | 15 | 72 | 6 | 100 | 6 | 128 | 6 | -15 | 0 | -20 | 0 | -15 | 0 | 136 | 0 | -9 | 0 | 136 | 0 | 9 | 0 | 128 | 6 | 100 | 6 | 72 | 6 | 15 | 0 | 20 | 0 | 15 | 0
3L13 | Lattice | Union electric company | Missouri, Nebraska, Minnesota | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 91.1594 | 65.1594 | 65.1594 | -17.6667 | -37 | -17 | 109 | -23.3333 | 109 | 23.3333 | 91.1594 | 65.1594 | 65.1594 | 17.6667 | 17 | 37 | 102 | 0 | 76 | 0 | 76 | 0 | -17 | -8 | -37 | 0 | -17 | 0 | 109 | 0 | -23 | -4 | 109 | 0 | 23 | 4 | 102 | 0 | 76 | 0 | 76 | 0 | 17 | 8 | 17 | 0 | 37 | 0
3L14 | Lattice | Texas electric service & Light Co | Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 77.1594 | 52.1594 | 52.1594 | -25.5833 | -37.8333 | -14.3333 | 103 | -15.6667 | 103 | 15.6667 | 77.1594 | 52.1594 | 52.1594 | 25.5833 | 14.3333 | 37.8333 | 88 | 0 | 63 | 0 | 63 | 0 | -25 | -7 | -37 | -10 | -14 | -4 | 103 | 0 | -15 | -8 | 103 | 0 | 15 | 8 | 88 | 0 | 63 | 0 | 63 | 0 | 25 | 7 | 14 | 4 | 37 | 10
3L15 | Lattice | Commonwealth Edison Company | Chicago | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 97.1594 | 54.1594 | 54.1594 | -28.5 | -40.5 | -16.5 | 117 | -40.5 | 117 | 40.5 | 97.1594 | 54.1594 | 54.1594 | 69 | 16.5 | 81 | 108 | 0 | 65 | 0 | 65 | 0 | -28.5 | 0 | -40.5 | 0 | -16.5 | 0 | 117 | 0 | -40.5 | 0 | 117 | 0 | 40.5 | 0 | 108 | 0 | 65 | 0 | 65 | 0 | 69 | 0 | 16.5 | 0 | 81 | 0
3P1 | Pole | Dayton Power & Light company | Ohio | 1 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 64.1594 | 75.6594 | 87.1594 | 9 | -9 | 9 | 131.5 | 0 | 0 | 0 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 75 | 0 | 86 | 6 | 98 | 0 | 9 | 0 | -9 | 0 | 9 | 0 | 131 | 6 | 0 | 0 | 0 | 0 | 0 | 0
3P2 | Pole | Cleveland electric iluminating, Indianapolis Power and Light Company, Northeast Utilities | Ohio, Indiana, New Hampshire, Massachusets, Connecticut | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 54.1594 | 77.1594 | 100.1594 | -15 | -15 | -15 | 132 | -14 | 132 | 14 | 100.1594 | 77.1594 | 54.1594 | 15 | 15 | 15 | 65 | 0 | 88 | 0 | 111 | 0 | -15 | 0 | -15 | 0 | -15 | 0 | 132 | 0 | -14 | 0 | 132 | 0 | 14 | 0 | 111 | 0 | 88 | 0 | 65 | 0 | 15 | 0 | 15 | 0 | 15 | 0
3P3 | Pole | Northern States Power Company, Wisconsin Electric Power Co | Minnesota, Wisconsin | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 90.1594 | 115.1594 | -14.25 | -21.25 | -14.25 | 135 | -17 | 135 | 17 | 115.1594 | 90.1594 | 65.1594 | 14.25 | 21.25 | 14.25 | 76 | 0 | 101 | 0 | 126 | 0 | -14 | -3 | -21 | -3 | -14 | -3 | 135 | 0 | -17 | 0 | 135 | 0 | 17 | 0 | 126 | 0 | 101 | 0 | 76 | 0 | 14 | 3 | 21 | 3 | 14 | 3
3P4 | Pole | Consolidated Edison Co, Houston Lightning Company, SouthWestern electric company | New York, Texas, Arkansas, Lousiana, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 81.1594 | 97.1594 | -11 | -11 | -11 | 111.5 | -8 | 111.5 | 8 | 97.1594 | 81.1594 | 65.1594 | 11 | 11 | 11 | 76 | 0 | 92 | 0 | 108 | 0 | -11 | 0 | -11 | 0 | -11 | 0 | 111 | 6 | -8 | 0 | 111 | 6 | 8 | 0 | 108 | 0 | 92 | 0 | 76 | 0 | 11 | 0 | 11 | 0 | 11 | 0
3P5 | Pole | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 72 | 97 | 122 | -11 | -19 | -11 | 140 | -7 | 140 | 7 | 122 | 97 | 72 | 11 | 19 | 11 | 82.8406 | 0 | 107.8406 | 0 | 132.8406 | 0 | -11 | 0 | -19 | 0 | -11 | 0 | 140 | 0 | -7 | 0 | 140 | 0 | 7 | 0 | 132.8406 | 0 | 107.8406 | 0 | 82.8406 | 0 | 11 | 0 | 19 | 0 | 11 | 0
3P6 | Pole | Dayton Power & Light company | Ohio | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 81.6594 | 104.1594 | -9 | -13 | -9 | 145.5 | 0 | 0 | 0 | 104.1594 | 81.6594 | 59.1594 | -9 | -13 | -9 | 70 | 0 | 92 | 6 | 114 | 12 | -9 | 0 | -13 | 0 | -9 | 0 | 144 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 12 | 92 | 6 | 70 | 0 | -9 | 0 | -13 | 0 | -9 | 0
3P7 | Pole | Illinois Power Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.826 | 80.826 | 80.826 | -15.5 | -41 | -16 | 127.6667 | -30 | 127.6667 | 30 | 116.826 | 80.826 | 80.826 | 15.5 | 16 | 41 | 127 | 8 | 91 | 8 | 91 | 8 | -15 | -6 | -41 | 0 | -16 | 0 | 127 | 8 | -30 | 0 | 127 | 8 | 30 | 0 | 127 | 8 | 91 | 8 | 91 | 8 | 15 | 6 | 16 | 0 | 41 | 0
3P8 | Pole | Commonwealth Edison Company | Chicago | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 98.1594 | 55.1594 | 55.1594 | -22 | -33 | -10 | 118 | 0 | 0 | 0 | 98.1594 | 55.1594 | 55.1594 | 22 | 10 | 33 | 109 | 0 | 66 | 0 | 66 | 0 | -22 | 0 | -33 | 0 | -10 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 66 | 0 | 66 | 0 | 22 | 0 | 10 | 0 | 33 | 0
3P8 | Pole |  |  | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 98.1594 | 55.1594 | 55.1594 | -22 | -33 | -10 | 118 | 0 | 0 | 0 | 98.1594 | 55.1594 | 55.1594 | 22 | 10 | 33 | 109 | 0 | 66 | 0 | 66 | 0 | -22 | 0 | -33 | 0 | -10 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 66 | 0 | 66 | 0 | 22 | 0 | 10 | 0 | 33 | 0
3H1 | H frame | Public Service Company of New Hampshire | New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -18 | 0 | 18 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -18 | 0 | 0 | 0 | 18 | 0 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H2 | H frame | Utah Power and Light Company | Utah | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 62.1594 | 62.1594 | 62.1594 | -27 | 0 | 27 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 73 | 0 | 73 | 0 | 73 | 0 | -26 | -12 | 0 | 0 | 26 | 12 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H3 | H frame | Niagara Mohawk Power Corporation, Illinois Power Company, Central Maine Power Co | New York, Illinois, Maine, Vermont, New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.826 | 44.826 | 44.826 | -26 | 0 | 26 | 65.5 | -13 | 65.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 8 | 55 | 8 | 55 | 8 | -26 | 0 | 0 | 0 | 26 | 0 | 64 | 18 | -13 | 0 | 64 | 18 | 13 | 0
3H4 | H frame | Public Service Company of New Hampshire, Northeast Utilities, New York State Electric & Gas, Vermont Electric Company, Wisconsin Public Service Corp | New Hampshire, Massachusets, Connecticut, New York, Vermont, Wisconsin | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 50.1594 | 50.1594 | 50.1594 | -26 | 0 | 26 | 73.5 | -13 | 73.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 61 | 0 | 61 | 0 | 61 | 0 | -26 | 0 | 0 | 0 | 26 | 0 | 73.5 | 0 | -13 | 0 | 73.5 | 0 | 13 | 0
3H5 | H frame | El paso electric company | Texas, New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 59.1594 | 52.6594 | -27 | 0 | 27 | 78 | -13.5 | 78 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 69 | 12 | 63 | 6 | -26 | -12 | 0 | 0 | 26 | 12 | 77 | 12 | -13.5 | 0 | 77 | 12 | 13.5 | 0
3H6 | H frame | Northern States Power Company, Wisconsin Electric Power Co, Kansas Gas & Electric Co | Minnesota, Wisconsin, Kansas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 46.6594 | 58.1594 | 46.6594 | -28.25 | 0 | 28.25 | 69 | -15.25 | 69 | 15.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 57 | 6 | 68 | 12 | 57 | 6 | -28 | -3 | 0 | 0 | 28 | 3 | 68 | 12 | -15 | -3 | 68 | 12 | 15 | 3
3H7 | H frame | Public Service Company of New Mexico | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -23.5 | 0 | 23.5 | 68.5 | -13.5 | 68.5 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -23 | -6 | 0 | 0 | 23 | 6 | 68 | 6 | -13.5 | 0 | 68 | 6 | 13.5 | 0
3H8 | H frame | Union electric company | Missouri, Nebraska, Minnesota | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 51.1594 | 51.1594 | 51.1594 | -24 | 0 | 24 | 72.5 | -26 | 72.5 | 26 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 62 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 72 | 6 | -26 | 0 | 72 | 6 | 26 | 0
3H9 | H frame | New Englad Electric System | New Englad, New Hampshire, Massachusets | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 52.6594 | 52.6594 | -20 | 0 | 20 | 74.5 | -9.5 | 74.5 | 9.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 63 | 6 | 63 | 6 | -19 | -12 | 0 | 0 | 19 | 12 | 74 | 6 | -9 | -6 | 74 | 6 | 9 | 6
3H10 | H frame | Boston Edison Company | Massachusets | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 96 | 70 | 70 | -10 | -32.75 | -10 | 111 | -27.25 | 111 | 27.25 | 96 | 70 | 70 | 10 | 10 | 32.75 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | -10 | 0 | -32 | -9 | -10 | 0 | 111 | 0 | -27 | -3 | 111 | 0 | 27 | 3 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | 10 | 0 | 10 | 0 | 32 | 9
3Y1 | Y | Tucson Gas & Electric Co | Arizona | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 109.2427 | 84.6594 | 84.6594 | 0 | -15 | 15 | 120.0833 | -13.5 | 120.0833 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 119 | 13 | 95 | 6 | 95 | 6 | 0 | 0 | -15 | 0 | 15 | 0 | 119 | 13 | -13.5 | 0 | 119 | 13 | 13.5 | 0
3Y2 | Y | Pacific Power Light corp |  | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -13.5 | 13.5 | 127 | -10 | 127 | 10 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -13 | -6 | 13 | 6 | 127 | 0 | -10 | 0 | 127 | 0 | 10 | 0
3Y3 | Y | SouthWestern electric company | Arkansas, Lousiana, Texas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -19.8333 | 19.8333 | 127 | -9 | 127 | 9 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -19.5 | -4 | 19.5 | 4 | 127 | 0 | -9 | 0 | 127 | 0 | 9 | 0
5L1 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 96.7889 | 69.2889 | 69.2889 | 0 | -20 | 20 | 122.25 | -13 | 122.25 | 13 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 112 | 6 | 85 | 0 | 85 | 0 | 0 | 0 | -20 | 0 | 20 | 0 | 121 | 15 | -13 | 0 | 121 | 15 | 13 | 0
5L2 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 98.2889 | 69.2889 | 69.2889 | 0 | -15.3333 | 15.3333 | 121 | -12 | 121 | 12 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 114 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -15 | -4 | 15 | 4 | 121 | 0 | -12 | 0 | 121 | 0 | 12 | 0
5L3 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 90.2889 | 74.2889 | 74.2889 | 0 | -29 | 29 | 106 | -15 | 106 | 15 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 106 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | -29 | 0 | 29 | 0 | 106 | 0 | -15 | 0 | 106 | 0 | 15 | 0
5L4 | Lattice | Basin Electric Power Co-op | California, North Dakota, South Dakota, Colorado, Montana, New Mexico, Wyoming, Minnesota, Iowa | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 85 | 69.2889 | 69.2889 | 0 | -28 | 28 | 99 | -26 | 99 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 100.7111 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -28 | 0 | 28 | 0 | 99 | 0 | -26 | 0 | 99 | 0 | 26 | 0
5L5 | Lattice | Carolina Power & Light Co | North Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 105 | 89.2889 | 89.2889 | 0 | -30.25 | 30.25 | 122.5 | -15.5 | 122.5 | 15.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120.7111 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -30 | -3 | 30 | 3 | 122 | 6 | -15.5 | 0 | 122 | 6 | 15.5 | 0
5L6 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 64.2889 | 64.2889 | 64.2889 | 0 | -35 | 35 | 95 | -25 | 95 | 25 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 95 | 0 | -25 | 0 | 95 | 0 | 25 | 0
5L7 | Lattice | Alabama Power Company, Baltimore Gas and Electric Company | Alabama, Maryland, | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -34 | 34 | 124 | -31 | 124 | 31 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -34 | 0 | 34 | 0 | 124 | 0 | -31 | 0 | 124 | 0 | 31 | 0
5L8 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -33 | 33 | 129 | -20 | 129 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -33 | 0 | 33 | 0 | 129 | 0 | -20 | 0 | 129 | 0 | 20 | 0
5L9 | Lattice | American Electric Power Co, Arizona Public Service Co, Duke Power Company | Virginia, Arizona, South Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 79.2889 | 79.2889 | 79.2889 | 0 | -32 | 32 | 109 | -24 | 109 | 24 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 0 | 0 | -32 | 0 | 32 | 0 | 109 | 0 | -24 | 0 | 109 | 0 | 24 | 0
5L10 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -35 | 35 | 137 | -26 | 137 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 137 | 0 | -26 | 0 | 137 | 0 | 26 | 0
5L11 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 100.2889 | 131.2889 | -15 | -25 | -15 | 172 | 0 | 0 | 0 | 131.2889 | 100.2889 | 69.2889 | 15 | 25 | 15 | 85 | 0 | 116 | 0 | 147 | 0 | -15 | 0 | -25 | 0 | -15 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 116 | 0 | 85 | 0 | 15 | 0 | 25 | 0 | 15 | 0
5L12 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 114.2889 | 69.2889 | 69.2889 | -27.75 | -40.5 | -15 | 150 | -18.5 | 150 | 18.5 | 114.2889 | 69.2889 | 69.2889 | 27.75 | 15 | 40.5 | 130 | 0 | 85 | 0 | 85 | 0 | -27 | -9 | -40 | -6 | -15 | 0 | 150 | 0 | -18.5 | 0 | 150 | 0 | 18.5 | 0 | 130 | 0 | 85 | 0 | 85 | 0 | 27 | 9 | 15 | 0 | 40 | 6
5L13 | Lattice |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 112.2889 | 74.2889 | 74.2889 | -18.5 | -46.5 | -18.5 | 140 | -12.125 | 140 | 15.125 | 112.2889 | 74.2889 | 74.2889 | 18.5 | 18.5 | 46.5 | 128 | 0 | 90 | 0 | 90 | 0 | -18 | -6 | -46 | -6 | -18 | -6 | 140 | 0 | -12 | -1.5 | 140 | 0 | 15 | 1.5 | 128 | 0 | 90 | 0 | 90 | 0 | 18 | 6 | 18 | 6 | 46 | 6
5L14 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | -42 | 0 | 42 | 128 | -21.8333 | 128 | 21.8333 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -42 | 0 | 0 | 0 | 42 | 0 | 128 | 0 | -21 | -10 | 128 | 0 | 21 | 10
5P1 | Pole |  |  | 1 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 99.2889 | 129.2889 | 18 | 21 | 18 | 160 | 4 | 0 | 0 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 85 | 0 | 115 | 0 | 145 | 0 | 18 | 0 | 21 | 0 | 18 | 0 | 160 | 0 | 4 | 0 | 0 | 0 | 0 | 0
5P2 | Pole |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 60.7056 | 73.2889 | 85.7056 | 18 | -17 | 18 | 120 | -10 | 120 | 10 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 77 | -7 | 90 | -12 | 102 | -7 | 18 | 0 | -17 | 0 | 18 | 0 | 120 | 0 | -10 | 0 | 120 | 0 | 10 | 0
5H1 | H frame | Baltimore Gas and Electric Company, Baltimore Gas and Electric Company | Maryland, Maryland | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 104.2889 | 104.2889 | 104.2889 | -35 | 0 | 35 | 129 | -26 | 129 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | -35 | 0 | 0 | 0 | 35 | 0 | 129 | 0 | -26 | 0 | 129 | 0 | 26 | 0
5H2 | H frame |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 123 | 87 | 87 | -30 | -45 | -15 | 149 | -32 | 149 | 32 | 123 | 87 | 87 | 15 | 45 | 15 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | -30 | 0 | -45 | 0 | -15 | 0 | 149 | 0 | -32 | 0 | 149 | 0 | 32 | 0 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | 15 | 0 | 45 | 0 | 15 | 0
5Y1 | Y |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 106.25 | 139.25 | 106.25 | -21.5 | 0 | 21.5 | 153 | -13.75 | 153 | 13.75 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 122.7111 | -9 | 155.7111 | -9 | 122.7111 | -9 | -21 | -6 | 0 | 0 | 21 | 6 | 153 | 0 | -13 | -9 | 153 | 0 | 13 | 9
5Y2 | Y | Arkansas Power & Light Co. | Arkansas | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 118.5 | 88 | 88 | 0 | -21.5 | 21.5 | 131.5 | -20 | 131.5 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 133.7111 | 6 | 103.7111 | 0 | 103.7111 | 0 | 0 | 0 | -21 | -6 | 21 | 6 | 131 | 6 | -20 | 0 | 131 | 6 | 20 | 0
5Y3 | Y | Alabama Power Company | Alabama | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 151.25 | 126 | 126 | 0 | -21 | 21 | 165.25 | -17.5 | 165.25 | 17.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 166.7111 | 3 | 141.7111 | 0 | 141.7111 | 0 | 0 | 0 | -21 | 0 | 21 | 0 | 165 | 3 | -17 | -6 | 165 | 3 | 17 | 6
7L1 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 92 | 92 | 92 | -44.5 | 0 | 44.5 | 127 | -36 | 127 | 36 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 115.0953 | 0 | 115.0953 | 0 | 115.0953 | 0 | -44 | -6 | 0 | 0 | 44 | 6 | 127 | 0 | -36 | 0 | 127 | 0 | 36 | 0
7L2 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 86.9047 | 86.9047 | 86.9047 | -45 | 0 | 45 | 138.6667 | -50 | 138.6667 | 50 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -45 | 0 | 0 | 0 | 45 | 0 | 138 | 8 | -50 | 0 | 138 | 8 | 50 | 0
7L3 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 135 | 135 | 135 | -41.8333 | 0 | 41.8333 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 158.0953 | 0 | 158.0953 | 0 | 158.0953 | 0 | -41 | -10 | 0 | 0 | 41 | 10 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7P1 | Pole |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 100.9047 | 100.9047 | 100.9047 | -39.3333 | 0 | 39.3333 | 145 | -66 | 145 | 66 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 124 | 0 | 124 | 0 | 124 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 145 | 0 | -66 | 0 | 145 | 0 | 66 | 0
7H1 | H frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 131 | 131 | 131 | -50 | 0 | 50 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 154.0953 | 0 | 154.0953 | 0 | 154.0953 | 0 | -50 | 0 | 0 | 0 | 50 | 0 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7V1 | V frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 110 | 110 | 110 | -39.3333 | 0 | 39.3333 | 150 | -30 | 150 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 133.0953 | 0 | 133.0953 | 0 | 133.0953 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 150 | 0 | -30 | 0 | 150 | 0 | 30 | 0
DC1 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0
DC2 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0

## Neighboring
number | state | abreviation | bordering_states | n_bordering_states
1 | Alabama | AL | Mississippi, Tennessee, Florida, Georgia | 4
2 | Alaska | AK | None | 0
3 | Arizona | AZ | Nevada, New Mexico, Utah, California, Colorado | 5
4 | Arkansas | AR | Oklahoma, Tennessee, Texas, Louisiana, Mississippi, Missouri | 6
5 | California | CA | Oregon, Arizona, Nevada | 3
6 | Colorado | CO | New Mexico, Oklahoma, Utah, Wyoming, Arizona, Kansas, Nebraska | 7
7 | Connecticut | CT | New York, Rhode Island, Massachusetts | 3
8 | Delaware | DE | New Jersey, Pennsylvania, Maryland | 3
9 | Florida | FL | Georgia, Alabama | 2
10 | Georgia | GA | North Carolina, South Carolina, Tennessee, Alabama, Florida | 5
11 | Hawaii | HI | None | 0
12 | Idaho | ID | Utah, Washington, Wyoming, Montana, Nevada, Oregon | 6
13 | Illinois | IL | Kentucky, Missouri, Wisconsin, Indiana, Iowa, Michigan (water border only) | 6
14 | Indiana | IN | Michigan, Ohio, Illinois, Kentucky | 4
15 | Iowa | IA | Nebraska, South Dakota, Wisconsin, Illinois, Minnesota, Missouri | 6
16 | Kansas | KS | Nebraska, Oklahoma, Colorado, Missouri | 4
17 | Kentucky | KY | Tennessee, Virginia, West Virginia, Illinois, Indiana, Missouri, Ohio | 7
18 | Louisiana | LA | Texas, Arkansas, Mississippi | 3
19 | Maine | ME | New Hampshire | 1
20 | Maryland | MD | Virginia, West Virginia, Delaware, Pennsylvania | 4
21 | Massachusetts | MA | New York, Rhode Island, Vermont, Connecticut, New Hampshire | 5
22 | Michigan | MI | Ohio, Wisconsin, Illinois, Indiana, Minnesota (water border) | 5
23 | Minnesota | MN | North Dakota, South Dakota, Wisconsin, Iowa, Michigan (water border) | 5
24 | Mississippi | MS | Louisiana, Tennessee, Alabama, Arkansas | 4
25 | Missouri | MO | Nebraska, Oklahoma, Tennessee, Arkansas, Illinois, Iowa, Kansas, Kentucky | 8
26 | Montana | MT | South Dakota, Wyoming, Idaho, North Dakota | 4
27 | Nebraska | NE | Missouri, South Dakota, Wyoming, Colorado, Iowa, Kansas, | 6
28 | Nevada | NV | Idaho, Oregon, Utah, Arizona, California | 5
29 | New Hampshire | NH | Vermont, Maine, Massachusetts | 3
30 | New Jersey | NJ | Pennsylvania, Delaware, New York | 3
31 | New Mexico | NM | Oklahoma, Texas, Utah, Arizona, Colorado | 5
32 | New York | NY | Pennsylvania, Rhode Island (water border), Vermont, Connecticut, Massachusetts, New Jersey | 6
33 | North Carolina | NC | Tennessee, Virginia, Georgia, South Carolina | 4
34 | North Dakota | ND | South Dakota, Minnesota, Montana | 3
35 | Ohio | OH | Michigan, Pennsylvania, West Virginia, Indiana, Kentucky | 5
36 | Oklahoma | OK | Missouri, New Mexico, Texas, Arkansas, Colorado, Kansas | 6
37 | Oregon | OR | Nevada, Washington, California, Idaho | 4
38 | Pennsylvania | PA | New York, Ohio, West Virginia, Delaware, Maryland, New Jersey | 6
39 | Rhode Island | RI | Massachusetts, New York (water border), Connecticut | 3
40 | South Carolina | SC | North Carolina, Georgia, | 2
41 | South Dakota | SD | Nebraska, North Dakota, Wyoming, Iowa, Minnesota, Montana | 6
42 | Tennessee | TN | Mississippi, Missouri, North Carolina, Virginia, Alabama, Arkansas, Georgia, Kentucky | 8
43 | Texas | TX | New Mexico, Oklahoma, Arkansas, Louisiana | 4
44 | Utah | UT | Nevada, New Mexico, Wyoming, Arizona, Colorado, Idaho | 6
45 | Vermont | VT | New Hampshire, New York, Massachusetts | 3
46 | Virginia | VA | North Carolina, Tennessee, West Virginia, Kentucky, Maryland | 5
47 | Washington | WA | Oregon, Idaho | 2
48 | West Virginia | WV | Pennsylvania, Virginia, Kentucky, Maryland, Ohio | 5
49 | Wisconsin | WI | Michigan, Minnesota, Illinois, Iowa | 4
50 | Wyoming | WY | Nebraska, South Dakota, Utah, Colorado, Idaho, Montana | 6

## TL_data_set
code | structure_type | company | state | miles | voltage_kv | conductor_type | conductor_name | Flag_cond_dataset | conductor_diameter_inch | conductor_kcmil | conductor_stranding | bundling | bundling_spacing_inch | ground_Type | ground_diameter_inch | ground_kcmil
3L8 | Lattice | American Electric Co. | Michigan | 188 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3L11 | Lattice | Boston Edison Company | Massachusetts | 18 | 345 | ACAR | 1700 | 0 | 1.504 | 1700 | 48/13 | 2 | 18 | Alumoweld | 0.343 | 117.649
3H10 | H Frame | Boston Edison Company | Massachusetts | 33 | 345 | ACSR | Falcon | 1 | 1.545 | 1590 | 54/19 | 2 | 18 | Alumoweld | 0.343 | 117.649
3H3 | H Frame | Central Maine Power Co | Maine | 86.8 | 345 | AAC | Hawthorn | 0 | 1.1 | 1192.5 | 61/0 | 2 | 18 | Alumoweld | 0.385 | 148.225
3P2 | Pole | Cleveland Electric Iluminating Co | Ohio | 18 | 345 | ACSR | Cardinal | 1 | 1.175 | 954 | 48/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3L6 | Lattice | Cleveland Electric Iluminating Co | Ohio | 44 | 345 | ACSR | Cardinal | 1 | 1.175 | 957 | 48/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3L15 | Lattice | Commonwealth Edison Company | Illinois | 104 | 345 | ACAR | 1277 | 0 | 1.302 | 1277 | 54/7 | 2 | 18 | Alumoweld | 0.349 | 121.801
3P8 | Pole | Commonwealth Edison Company | Illinois | 54 | 345 | ACAR | 1277 | 0 | 1.302 | 1277 | 54/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3P4 | Pole | Consolidated Edison Co of New York | New York | 19 | 345 | ACAR | 2500 | 0 | 1.821 | 2500 | 54/37 | 2 | 18 | Alumoweld | 0.5625 | 316.4062
3L11 | Lattice | Consolidated Edison Co of New York | New York | 25 | 345 | ACAR | 2500 | 0 | 1.821 | 2500 | 54/37 | 2 | 18 | Alumoweld | 0.5625 | 316.4062
3L7 | Lattice | Consolidated Edison Co of New York | New York | 150 | 345 | ACSR | Kiwi | 0 | 1.82 | 2167 | 72/7 | 2 | 18 | Alumoweld | 0.5625 | 316.4062
3L3 | Lattice | Consumers Power Company | Michigan | 253 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Steel | 0.4375 | 191.4062 | 7/16
3L9 | Lattice | Consumers Power Company | Michigan | 377 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Steel | 0.4375 | 191.4062 | 7/16
3L9 | Lattice | Consumers Power Company | Michigan | 161.6 | 345 | ACSR | Bobolink | 1 | 1.427 | 1431 | 45/7 | 2 | 18 | Steel | 0.4375 | 191.4062 | 7/16
3P6 | Pole | Dayton Power & Light Company | Ohio | 24.5 | 345 | ACAR | 1024.5 | 0 | 1.165 | 1024.5 | 30/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3P1 | Pole | Dayton Power & Light Company | Ohio | 21.8 | 345 | ACAR | 1024.5 | 0 | 1.165 | 1024.5 | 30/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3L10 | Lattice | Detroit Edison | Michigan | 130 | 345 | ACSR | Bobolink | 1 | 1.427 | 1431 | 45/7 | 2 | 18 | ACSR | 0.576 | 331.776
3H5 | H Frame | El Paso Electric Copany | New Mexico | 230 | 345 | ACSR | Tern | 1 | 1.063 | 795 | 45/7 | 2 | 18 | Galv Steel | 0.375 | 140.625 | 3/8
3P4 | Pole | Houston Lightinh & Power Company | Texas | 1.6 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3L11 | Lattice | Houston Lightinh & Power Company | Texas | 18 | 345 | ACSR | Kiwi | 0 | 1.737 | 2167 | 72/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3L11 | Lattice | Houston Lightinh & Power Company | Texas | 46 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3H3 | H Frame | Illinois Power Company | Illinois | 356 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | Alumoweld | 0.385 | 148.225
3P7 | Pole | Illinois Power Company | Illinois | 15.5 | 345 | ACSR | Falcon | 1 | 1.293 | 1590 | 54/19 | 2 | 18 | Alumoweld | 0.433 | 187.489
3L2 | Lattice | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3L9 | Lattice | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3P2 | Pole | Indianapolis Power & Light Company | Indiana | 368 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3L1 | Lattice | Iowa Public Service Co | Iowa | 76 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3H6 | H Frame | Kansas Gas & Electric Co | Kansas | 600 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3H9 | H Frame | New Englad Electric System | New Hampshire | 36 | 345 | AAC | Marigold | 0 | 1.216 | 1113 | 61/0 | 2 | 16 | Alumoweld | 0.343 | 117.649
3H4 | H Frame | New York State Electric & Gas | New York | 220 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | EHS steel | 0.4375 | 191.4062 | 7/16
3H4 | H Frame | New York State Electric & Gas | New York | 56.9 | 345 | ACSR | Ortolan | 1 | 1.212 | 1033.5 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16
3H3 | H Frame | Niagara Mohawk Power Corp. | New York | 83 | 345 | ACSR | Bunting | 0 | 1.302 | 1192.5 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16
3H4 | H Frame | Northeast Utilities | Connecticut | 275 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | Alumoweld | 0.375 | 140.625
3P2 | Pole | Northeast Utilities | Connecticut | 11.8 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | Alumoweld | 0.375 | 140.625
3L5 | Lattice | Northern Indiana Public Service Co | Indiana | 19.45 | 345 | ACSR | Bluebird | 1 | 1.762 | 3104.644 | 84/19 | 1 | 0 | EHS steel | 0.4375 | 191.4062 | 7/16
3H6 | H Frame | Northern States Power Company | Minnesota | 336.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3P3 | Pole | Northern States Power Company | Minnesota | 96.4 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | Alumoweld | 0.385 | 148.225
3L8 | Lattice | Oklahoma Gas & Electric Co. | Oklahoma | 230.9 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3Y2 | Y | Pacific Power & Light Co. | Wyoming | 471.2 | 345 | ACSR | Skylark | 0 | 1.316 | 1272 | 36/1 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3L4 | Lattice | Pennsylvania Electric Co. | Pennsylvania | 27.3 | 345 | ACSR | Curlew | 1 | 1.246 | 1033.5 | 54/7 | 2 | 18 | EHS steel | 15.5 | 240250 | 3/8
3H4 | H Frame | Public Service Company of New Hampshire | New Hampshire | 23.6 | 345 | ACSR | Finch | 1 | 1.293 | 1113 | 54/19 | 2 | 18 | Alumoweld | 0.385 | 148.225
3H1 | H Frame | Public Service Company of New Hampshire | New Hampshire | 17 | 345 | ACSR | Finch | 1 | 1.293 | 1113 | 54/19 | 2 | 18 | Alumoweld | 0.385 | 148.225
3H1 | H Frame | Public Service Company of New Hampshire | New Hampshire | 36.4 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 2 | 18 | Alumoweld | 0.385 | 148.225
3H7 | H Frame | Public Service Co. of New Mexico | New Mexico | 160 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3Y3 | Y | Southwestern Electric Power Company | Louisiana | 64.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | Alumoweld | 0.433 | 187.489
3P4 | Pole | Southwestern Electric Power Company | Louisiana | 7.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3Y3 | Y | Southwestern Electric Power Company | Louisiana | 73.4 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 54/19 | 1 | 0 | Alumoweld | 0.433 | 187.489
3L14 | Lattice | Texas Electric Service Co. | Texas | 240.5 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3L14 | Lattice | Texas Power & Light Co. | Texas | 68.8 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16
3Y1 | Y | Tucson Gas & Electric Co. | Arizona | 413 | 345 | ACSR | Rail | 1 | 1.165 | 954 | 45/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3H8 | H Frame | Union Electric Company | Missouri | 186 | 345 | ACSR | Tern | 1 | 1.063 | 795 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16
3L13 | Lattice | Union Electric Company | Missouri | 23 | 345 | ACSR | Lapwing | 1 | 1.504 | 1590 | 45/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16
3L12 | Lattice | Utah Power and Light Company | Utah | 45 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | EHS steel | 0.5 | 250 | 1/2
3P5 | Pole | Utah Power and Light Company | Utah | 61 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | EHS steel | 0.5 | 250 | 1/2
3H2 | H Frame | Utah Power and Light Company | Utah | 248 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | Alumoweld | 0.475 | 225.625
3H4 | H Frame | Vermont Electric Company | Vermont | 51.3 | 345 | ACAR | 927.2 | 0 | 1.108 | 927.2 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8
3L2 | Lattice | Western Area Power Administration | Colorado | 141 | 345 | ACSR | Bittern | 1 | 1.345 | 1272 | 45/7 | 2 | 18 | Steel | 0.5 | 250
3L2 | Lattice | Western Area Power Administration | Colorado | 419 | 345 | ACSR | Cardinal | 1 | 1.196 | 954 | 54/7 | 2 | 18 | EHS steel | 0.4375 | 191.4062 | 7/16
3P3 | Pole | Wisconsin Electric Power Co | Wisconsin | 28 | 345 | ACSR | Bluebird | 1 | 1.762 | 2156 | 84/19 | 1 | 0 | ACSR Guinea | 0.576 | 159
3H4 | H Frame | Wisconsin Public Service Corp | Wisconsin | 28.8 | 345 | ACSR | Drake | 1 | 1.108 | 795 | 26/7 | 2 | 18 | EHS steel | 0.375 | 140.625 | 3/8

## Conductors
conductor_type | codeword | Size_kcmil | stranding | diameter_inch | R_20DC_ohm_kft | R_25AC_ohm_kft | R_50AC_ohm_kft | R_75AC_ohm_kft | C_60Hz_Mohm_kft | L_60Hz_25C_ohm_kft | L_60Hz_50C_ohm_kft | L_60Hz_75C_ohm_kft | Ampacity (A)
ACSR | Waxwing | 266.8 | 18/1 | 0.609 | 0.0644 | 0.0657 | 0.0723 | 0.0788 | 0.576 | 0.0903 | 0.0903 | 0.0903 | 445 | 0.47678
ACSR | Partridge | 266.8 | 26/7 | 0.642 | 0.0637 | 0.0652 | 0.0714 | 0.0778 | 0.565 | 0.0881 | 0.0881 | 0.0881 | 455 | 0.46517
ACSR | Merlin | 336.4 | 18/1 | 0.684 | 0.051 | 0.0523 | 0.0574 | 0.0625 | 0.56 | 0.0826 | 0.0826 | 0.0826 | 515 | 0.43613
ACSR | Linnet | 336.4 | 26/7 | 0.721 | 0.0506 | 0.0517 | 0.0568 | 0.0619 | 0.549 | 0.0854 | 0.0854 | 0.0854 | 530 | 0.45091
ACSR | Oriole | 336.4 | 30/7 | 0.741 | 0.0502 | 0.0513 | 0.0563 | 0.0614 | 0.544 | 0.0843 | 0.0843 | 0.0843 | 530 | 0.4451
ACSR | Chickadee | 397.5 | 18/1 | 0.743 | 0.0432 | 0.0443 | 0.0487 | 0.0528 | 0.544 | 0.0856 | 0.0856 | 0.0856 | 575 | 0.45197
ACSR | Ibis | 397.5 | 26/7 | 0.783 | 0.0428 | 0.0438 | 0.0481 | 0.0525 | 0.539 | 0.0835 | 0.0835 | 0.0835 | 590 | 0.44088
ACSR | Pelican | 477 | 18/1 | 0.814 | 0.036 | 0.0369 | 0.0405 | 0.0441 | 0.528 | 0.0835 | 0.0835 | 0.0835 | 640 | 0.44088
ACSR | Flicker | 477 | 24/7 | 0.846 | 0.0358 | 0.0367 | 0.0403 | 0.0439 | 0.524 | 0.0818 | 0.0818 | 0.0818 | 670 | 0.4319
ACSR | Hawk | 477 | 26/7 | 0.858 | 0.0357 | 0.0366 | 0.0402 | 0.0438 | 0.522 | 0.0814 | 0.0814 | 0.0814 | 660 | 0.42979
ACSR | Hen | 477 | 30/7 | 0.883 | 0.0354 | 0.0362 | 0.0398 | 0.0434 | 0.517 | 0.0803 | 0.0803 | 0.0803 | 660 | 0.42398
ACSR | Osprey | 556.5 | 18/1 | 0.879 | 0.0309 | 0.0318 | 0.0348 | 0.0379 | 0.518 | 0.0818 | 0.0818 | 0.0818 | 710 | 0.4319
ACSR | Parakeet | 556.5 | 24/7 | 0.914 | 0.0307 | 0.0314 | 0.0347 | 0.0377 | 0.512 | 0.0801 | 0.0801 | 0.0801 | 720 | 0.42293
ACSR | Dove | 556.5 | 26/7 | 0.927 | 0.0305 | 0.0314 | 0.0345 | 0.0375 | 0.51 | 0.0795 | 0.0795 | 0.0795 | 730 | 0.41976
ACSR | Rook | 636 | 24/7 | 0.977 | 0.0268 | 0.0277 | 0.0303 | 0.033 | 0.502 | 0.0786 | 0.0786 | 0.0786 | 780 | 0.41501
ACSR | Grosbeak | 636 | 26/7 | 0.99 | 0.0267 | 0.0275 | 0.0301 | 0.0328 | 0.499 | 0.078 | 0.078 | 0.078 | 790 | 0.41184
ACSR | Drake | 795 | 26/7 | 1.108 | 0.0214 | 0.0222 | 0.0242 | 0.0263 | 0.482 | 0.0756 | 0.0756 | 0.0756 | 910 | 0.39917
ACSR | Tern | 795 | 45/7 | 1.063 | 0.0216 | 0.0225 | 0.0246 | 0.0267 | 0.488 | 0.0769 | 0.0769 | 0.0769 | 890 | 0.40603
ACSR | Rail | 954 | 45/7 | 1.165 | 0.018 | 0.0188 | 0.0206 | 0.0223 | 0.474 | 0.0748 | 0.0748 | 0.0748 | 970 | 0.39494
ACSR | Cardinal | 954 | 54/7 | 1.196 | 0.0179 | 0.0186 | 0.0205 | 0.0222 | 0.47 | 0.0737 | 0.0737 | 0.0737 | 990 | 0.38914
ACSR | Ortolan | 1033.5 | 45/7 | 1.213 | 0.0167 | 0.0175 | 0.02022 |  | 0.46728 | 0.073864 | 0.073864 | 0.073864 | 1030 | 0.39 | From Stevenson
ACSR | Curlew | 1033.5 | 54/7 | 1.246 | 0.0165 | 0.0172 | 0.0189 | 0.0205 | 0.464 | 0.0729 | 0.0729 | 0.0729 | 1040 | 0.38491 | Not in ASTM B232
ACSR | Bluejay | 1113 | 45/7 | 1.259 | 0.0155 | 0.0163 | 0.0178 | 0.0193 | 0.461 | 0.0731 | 0.0731 | 0.0731 | 1070 | 0.38597
ACSR | Finch | 1113 | 54/19 | 1.293 | 0.0155 | 0.016212 | 0.017746 |  | 0.45725 | 0.07197 | 0.07197 | 0.07197 | 1070 | 0.38 | From Stevenson
ACSR | Bittern | 1272 | 45/7 | 1.345 | 0.0135 | 0.0144 | 0.0157 | 0.017 | 0.451 | 0.0716 | 0.0716 | 0.0716 | 1160 | 0.37805
ACSR | Pheasant | 1272 | 54/19 | 1.382 | 0.0135 | 0.014223 | 0.015549 |  | 0.44722 | 0.070455 | 0.070455 | 0.070455 | 1160 | 0.372 | From Stevenson
ACSR | Bobolink | 1431 | 45/7 | 1.427 | 0.0121 | 0.012955 | 0.014129 |  | 0.44194 | 0.070265 | 0.070265 | 0.070265 | 1200 | 0.371 | From Stevenson
ACSR | Plover | 1431 | 54/19 | 1.465 | 0.012 | 0.012746 | 0.01392 |  | 0.43771 | 0.069129 | 0.069129 | 0.069129 | 1250 | 0.365 | From Stevenson
ACSR | Lapwing | 1590 | 45/7 | 1.502 | 0.0108 | 0.0117 | 0.0128 | 0.0138 | 0.434 | 0.0689 | 0.0689 | 0.0689 | 1340 | 0.36379
ACSR | Falcon | 1590 | 54/19 | 1.545 | 0.0108 | 0.0116 | 0.0129 | 0.014 | 0.43 | 0.0678 | 0.0678 | 0.0678 | 1360 | 0.35798
ACSR | Bluebird | 2156 | 84/19 | 1.762 | 0.00801 | 0.00903 | 0.00977 | 0.0105 | 0.409 | 0.0652 | 0.0652 | 0.0652 | 1610 | 0.34426
AAC | Daisy | 266.8 |  |  | 0.0647 | 0.0663 | 0.0727 | 0.0794 | 0.581 | 0.0647 |  |  | 440 | 0.34162
AAC | Laurel | 266.8 |  |  | 0.0648 | 0.0663 | 0.0727 | 0.0794 | 0.581 | 0.0648 |  |  | 445 | 0.34214
AAC | Tulip | 336.4 |  |  | 0.0513 | 0.0527 | 0.0578 | 0.0629 | 0.56 | 0.0513 |  |  | 510 | 0.27086
AAC | Cosmos | 477 |  |  | 0.0363 | 0.0373 | 0.0409 | 0.0445 | 0.533 | 0.0363 |  |  | 640 | 0.19166
AAC | Syringa | 477 |  |  | 0.0363 | 0.0373 | 0.0409 | 0.0445 | 0.533 | 0.0363 |  |  | 640 | 0.19166
AAC | Zinnia | 500 |  |  | 0.0346 | 0.0356 | 0.039 | 0.0426 | 0.533 | 0.0346 |  |  | 660 | 0.18269
AAC | Dahlia | 556.5 |  |  | 0.0311 | 0.032 | 0.0352 | 0.0383 | 0.522 | 0.0311 |  |  | 700 | 0.16421
AAC | Orchid | 636 |  |  | 0.0272 | 0.0282 | 0.0309 | 0.0335 | 0.511 | 0.0272 |  |  | 760 | 0.14362
AAC | Violet | 715 |  |  | 0.0241 | 0.025 | 0.0275 | 0.0299 | 0.502 | 0.0241 |  |  | 820 | 0.12725
AAC | Arbutus | 795 |  |  | 0.0217 | 0.0227 | 0.0248 | 0.0269 | 0.494 | 0.0217 |  |  | 880 | 0.11458
AAC | Magnolia | 954 |  |  | 0.0181 | 0.0191 | 0.0208 | 0.0227 | 0.479 | 0.0181 |  |  | 980 | 0.095568
AAC | Bluebell | 1033.5 |  |  | 0.0167 | 0.0177 | 0.0193 | 0.021 | 0.473 | 0.0167 |  |  | 1030 | 0.088176
AAC | Columbine | 1351.5 |  |  | 0.0128 | 0.0138 | 0.0151 | 0.0163 | 0.452 | 0.0128 |  |  | 1210 | 0.067584
AAC | Coreopsis | 1590 |  |  | 0.0128 | 0.012 | 0.013 | 0.0141 | 0.439 | 0.0128 |  |  | 1230 | 0.067584
AAC | Cowslip | 2000 |  |  | 0.00865 | 0.00994 | 0.0107 | 0.0115 | 0.421 | 0.00865 |  |  | 1520 | 0.045672
AAC | Lupine | 2500 |  |  | 0.00699 | 0.00845 | 0.00907 | 0.0097 | 0.404 | 0.00699 |  |  | 1700 | 0.036907

## Validation
VALIDATIONS
Structure type | conductor_type
Lattice | AAC
Pole | ACSR
H Frame | AAAC
Y | ACAR

## Sources
Sources
Insulators string distance:IEC 60071-2 Insulation co-ordination application guite part 2 (creepage distance). AND IEC 60305 IEC Insulators classes
EPRI Transmission reference book
Stevenson, Grainger
| typical bundling | Oregon state U | Section 4 Transmission Lines.pdf (oregonstate.edu)

## TL_Geometry (2)
code | structure_type | company | state | n_circuits | n_ground_w | voltage_kv | Creep_Dist_mm_kv | Insul_Creep_Dist_mm | Insul_Spac_mm | L_Ins_String_ft | ha1t_ft | hb1t_ft | hc1t_ft | Sa1t_ft | Sb1t_ft | Sc1t_ft | hg11t_ft | Sg11t_ft | hg21t_ft | Sg21t_ft | ha2t_ft | hb2t_ft | hc2t_ft | Sa2t_ft | Sb2t_ft | Sc2t_ft | ha1 (ft) | ha1 (inch) | hb1 (ft) | hb1 (inch) | hc1 (ft) | hc1 (inch) | Sa1 (ft) | Sa1 (inch) | Sb1 (ft) | Sb1 (inch) | Sc1 (ft) | Sc1 (inch) | hg11 (ft) | hg11 (inch) | Sg11 (ft) | Sg11 (inch) | hg21 (ft) | hg21 (inch) | Sg21 (ft) | Sg21 (inch) | ha2 (ft) | ha2 (inch) | hb2 (ft) | hb2 (inch) | hc2 (ft) | hc2 (inch) | Sa2 (ft) | Sa2 (inch) | Sb2 (ft) | Sb2 (inch) | Sc2 (ft) | Sc2 (inch)
3L1 | Lattice | Iowa Public Service Co | Iowa | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -23.75 | 0 | 23.75 | 87.5 | -17.8125 | 87.5 | 17.8125 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -23 | -9 | 0 | 0 | 23 | 9 | 87 | 6 | -17.25 | -6.75 | 87 | 6 | 17.25 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L2 | Lattice | Indianapolis Power and Light Company, Western Power Area Administration | Indiana, Colorado | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 69.1594 | 69.1594 | -32 | 0 | 32 | 96.5 | -21.5 | 96.5 | 21.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | -32 | 0 | 0 | 0 | 32 | 0 | 96 | 6 | -21 | -6 | 96 | 6 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3L3 | Lattice | Consumers Power Company | Michigan | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 59.1594 | 59.1594 | -24.5 | 0 | 24.5 | 87.5 | -16.5 | 87.5 | 16.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 70 | 0 | -24 | -6 | 0 | 0 | 24 | 6 | 87 | 6 | -16 | -6 | 87 | 6 | 16 | 6
3L4 | Lattice | Pennsylvania Electric Co | Pensylvania | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.1594 | 44.1594 | 44.1594 | -22.6667 | 0 | 22.6667 | 73 | -18.5833 | 73 | 18.5833 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 0 | 55 | 0 | 55 | 0 | -22 | -8 | 0 | 0 | 22 | 8 | 73 | 0 | -18 | -7 | 73 | 0 | 18 | 7
3L5 | Lattice | Northern Indiana Public Service | Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 79.1594 | 79.1594 | 79.1594 | -24 | 0 | 24 | 102 | -21.6 | 102 | 21.6 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 90 | 0 | 90 | 0 | 90 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 102 | 0 | -21.6 | 0 | 102 | 0 | 21.6 | 0
3L6 | Lattice | Cleveland electric iluminating | Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 43.6594 | 43.6594 | 43.6594 | -23 | 0 | 23 | 94.5 | -20.5 | 94.5 | 20.5 | 72.1594 | 72.1594 | 72.1594 | 23 | 0 | -23 | 54 | 6 | 54 | 6 | 54 | 6 | -23 | 0 | 0 | 0 | 23 | 0 | 93 | 18 | -20 | -6 | 93 | 18 | 20 | 6 | 82 | 12 | 82 | 12 | 82 | 12 | 23 | 0 | 0 | 0 | -23 | 0
3L7 | Lattice | Consolidated Edison Co | New York | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 41.826 | 64.826 | 87.826 | -19 | -17.5 | -15.3333 | 104.6667 | -12 | 104.6667 | 12 | 87.826 | 64.826 | 41.826 | 15.3333 | 17.5 | 19 | 52 | 8 | 75 | 8 | 98 | 8 | -19 | 0 | -17 | -6 | -15 | -4 | 104 | 8 | -12 | 0 | 104 | 8 | 12 | 0 | 98 | 8 | 75 | 8 | 52 | 8 | 15 | 4 | 17 | 6 | 19 | 0
3L8 | Lattice | Oklahoma Gas & Electric Co, American Electric Power Co | Oklahoma, Ohio | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 93.1594 | 117.1594 | -22 | -37 | -22 | 142 | -11 | 142 | 11 | 117.1594 | 93.1594 | 69.1594 | 22 | 37 | 22 | 80 | 0 | 104 | 0 | 128 | 0 | -22 | 0 | -37 | 0 | -22 | 0 | 142 | 0 | -11 | 0 | 142 | 0 | 11 | 0 | 128 | 0 | 104 | 0 | 80 | 0 | 22 | 0 | 37 | 0 | 22 | 0
3L9 | Lattice | Consumers Power Company, Indianapolis Power and Light Company | Michigan, Indiana | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 69.1594 | 89.1594 | 111.1594 | -18 | -29 | -17 | 137 | -24 | 137 | 24 | 111.1594 | 89.1594 | 69.1594 | 17 | 29 | 18 | 80 | 0 | 100 | 0 | 122 | 0 | -18 | 0 | -29 | 0 | -17 | 0 | 137 | 0 | -24 | 0 | 137 | 0 | 24 | 0 | 122 | 0 | 100 | 0 | 80 | 0 | 17 | 0 | 29 | 0 | 18 | 0
3L10 | Lattice | Detroit Edison | Michigan | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 53.1594 | 74.6594 | 98.6594 | -20.5 | -27 | -18.5 | 119.5 | -25.75 | 119.5 | 25.75 | 98.6594 | 74.6594 | 53.1594 | 18.5 | 27 | 20.5 | 64 | 0 | 85 | 6 | 109 | 6 | -20 | -6 | -27 | 0 | -18 | -6 | 119 | 6 | -25 | -9 | 119 | 6 | 25 | 9 | 109 | 6 | 85 | 6 | 64 | 0 | 18 | 6 | 27 | 0 | 20 | 6
3L13 | Lattice | Union electric company | Missouri, Nebraska, Minnesota | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 91.1594 | 65.1594 | 65.1594 | -17.6667 | -37 | -17 | 109 | -23.3333 | 109 | 23.3333 | 91.1594 | 65.1594 | 65.1594 | 17.6667 | 17 | 37 | 102 | 0 | 76 | 0 | 76 | 0 | -17 | -8 | -37 | 0 | -17 | 0 | 109 | 0 | -23 | -4 | 109 | 0 | 23 | 4 | 102 | 0 | 76 | 0 | 76 | 0 | 17 | 8 | 17 | 0 | 37 | 0
3L14 | Lattice | Texas electric service & Light Co | Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 77.1594 | 52.1594 | 52.1594 | -25.5833 | -37.8333 | -14.3333 | 103 | -15.6667 | 103 | 15.6667 | 77.1594 | 52.1594 | 52.1594 | 25.5833 | 14.3333 | 37.8333 | 88 | 0 | 63 | 0 | 63 | 0 | -25 | -7 | -37 | -10 | -14 | -4 | 103 | 0 | -15 | -8 | 103 | 0 | 15 | 8 | 88 | 0 | 63 | 0 | 63 | 0 | 25 | 7 | 14 | 4 | 37 | 10
3L15 | Lattice | Commonwealth Edison Company | Chicago | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 97.1594 | 54.1594 | 54.1594 | -28.5 | -40.5 | -16.5 | 117 | -40.5 | 117 | 40.5 | 97.1594 | 54.1594 | 54.1594 | 69 | 16.5 | 81 | 108 | 0 | 65 | 0 | 65 | 0 | -28.5 | 0 | -40.5 | 0 | -16.5 | 0 | 117 | 0 | -40.5 | 0 | 117 | 0 | 40.5 | 0 | 108 | 0 | 65 | 0 | 65 | 0 | 69 | 0 | 16.5 | 0 | 81 | 0
3P1 | Pole | Dayton Power & Light company | Ohio | 1 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 64.1594 | 75.6594 | 87.1594 | 9 | -9 | 9 | 131.5 | 0 | 0 | 0 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 75 | 0 | 86 | 6 | 98 | 0 | 9 | 0 | -9 | 0 | 9 | 0 | 131 | 6 | 0 | 0 | 0 | 0 | 0 | 0
3P2 | Pole | Cleveland electric iluminating, Indianapolis Power and Light Company, Northeast Utilities | Ohio, Indiana, New Hampshire, Massachusets, Connecticut | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 54.1594 | 77.1594 | 100.1594 | -15 | -15 | -15 | 132 | -14 | 132 | 14 | 100.1594 | 77.1594 | 54.1594 | 15 | 15 | 15 | 65 | 0 | 88 | 0 | 111 | 0 | -15 | 0 | -15 | 0 | -15 | 0 | 132 | 0 | -14 | 0 | 132 | 0 | 14 | 0 | 111 | 0 | 88 | 0 | 65 | 0 | 15 | 0 | 15 | 0 | 15 | 0
3P3 | Pole | Northern States Power Company, Wisconsin Electric Power Co | Minnesota, Wisconsin | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 90.1594 | 115.1594 | -14.25 | -21.25 | -14.25 | 135 | -17 | 135 | 17 | 115.1594 | 90.1594 | 65.1594 | 14.25 | 21.25 | 14.25 | 76 | 0 | 101 | 0 | 126 | 0 | -14 | -3 | -21 | -3 | -14 | -3 | 135 | 0 | -17 | 0 | 135 | 0 | 17 | 0 | 126 | 0 | 101 | 0 | 76 | 0 | 14 | 3 | 21 | 3 | 14 | 3
3P4 | Pole | Consolidated Edison Co, Houston Lightning Company, SouthWestern electric company | New York, Texas, Arkansas, Lousiana, Texas | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 65.1594 | 81.1594 | 97.1594 | -11 | -11 | -11 | 111.5 | -8 | 111.5 | 8 | 97.1594 | 81.1594 | 65.1594 | 11 | 11 | 11 | 76 | 0 | 92 | 0 | 108 | 0 | -11 | 0 | -11 | 0 | -11 | 0 | 111 | 6 | -8 | 0 | 111 | 6 | 8 | 0 | 108 | 0 | 92 | 0 | 76 | 0 | 11 | 0 | 11 | 0 | 11 | 0
3P5 | Pole | Utah Power and Light Company | Utah | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 72 | 97 | 122 | -11 | -19 | -11 | 140 | -7 | 140 | 7 | 122 | 97 | 72 | 11 | 19 | 11 | 82.8406 | 0 | 107.8406 | 0 | 132.8406 | 0 | -11 | 0 | -19 | 0 | -11 | 0 | 140 | 0 | -7 | 0 | 140 | 0 | 7 | 0 | 132.8406 | 0 | 107.8406 | 0 | 82.8406 | 0 | 11 | 0 | 19 | 0 | 11 | 0
3P6 | Pole | Dayton Power & Light company | Ohio | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 59.1594 | 81.6594 | 104.1594 | -9 | -13 | -9 | 145.5 | 0 | 0 | 0 | 104.1594 | 81.6594 | 59.1594 | -9 | -13 | -9 | 70 | 0 | 92 | 6 | 114 | 12 | -9 | 0 | -13 | 0 | -9 | 0 | 144 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 12 | 92 | 6 | 70 | 0 | -9 | 0 | -13 | 0 | -9 | 0
3P7 | Pole | Illinois Power Company | Illinois | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.826 | 80.826 | 80.826 | -15.5 | -41 | -16 | 127.6667 | -30 | 127.6667 | 30 | 116.826 | 80.826 | 80.826 | 15.5 | 16 | 41 | 127 | 8 | 91 | 8 | 91 | 8 | -15 | -6 | -41 | 0 | -16 | 0 | 127 | 8 | -30 | 0 | 127 | 8 | 30 | 0 | 127 | 8 | 91 | 8 | 91 | 8 | 15 | 6 | 16 | 0 | 41 | 0
3P8 | Pole | Commonwealth Edison Company | Chicago | 2 | 1 | 345 | 20 | 355 | 170 | 10.8406 | 98.1594 | 55.1594 | 55.1594 | -22 | -33 | -10 | 118 | 0 | 0 | 0 | 98.1594 | 55.1594 | 55.1594 | 22 | 10 | 33 | 109 | 0 | 66 | 0 | 66 | 0 | -22 | 0 | -33 | 0 | -10 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 66 | 0 | 66 | 0 | 22 | 0 | 10 | 0 | 33 | 0
3H1 | H frame | Public Service Company of New Hampshire | New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -18 | 0 | 18 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -18 | 0 | 0 | 0 | 18 | 0 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H2 | H frame | Utah Power and Light Company | Utah | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 62.1594 | 62.1594 | 62.1594 | -27 | 0 | 27 | 73 | -12.25 | 73 | 12.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 73 | 0 | 73 | 0 | 73 | 0 | -26 | -12 | 0 | 0 | 26 | 12 | 73 | 0 | -12 | -3 | 73 | 0 | 12 | 3
3H3 | H frame | Niagara Mohawk Power Corporation, Illinois Power Company, Central Maine Power Co | New York, Illinois, Maine, New Englad | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 44.826 | 44.826 | 44.826 | -26 | 0 | 26 | 65.5 | -13 | 65.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 55 | 8 | 55 | 8 | 55 | 8 | -26 | 0 | 0 | 0 | 26 | 0 | 64 | 18 | -13 | 0 | 64 | 18 | 13 | 0
3H4 | H frame | Public Service Company of New Hampshire, Northeast Utilities, New York State Electric & Gas, Vermont Electric Company, Wisconsin Public Service Corp | New Hampshire, Massachusets, Connecticut, New York, Vermont, Wisconsin | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 50.1594 | 50.1594 | 50.1594 | -26 | 0 | 26 | 73.5 | -13 | 73.5 | 13 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 61 | 0 | 61 | 0 | 61 | 0 | -26 | 0 | 0 | 0 | 26 | 0 | 73.5 | 0 | -13 | 0 | 73.5 | 0 | 13 | 0
3H5 | H frame | El paso electric company | Texas, New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 59.1594 | 52.6594 | -27 | 0 | 27 | 78 | -13.5 | 78 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 69 | 12 | 63 | 6 | -26 | -12 | 0 | 0 | 26 | 12 | 77 | 12 | -13.5 | 0 | 77 | 12 | 13.5 | 0
3H6 | H frame | Northern States Power Company, Wisconsin Electric Power Co, Kansas Gas & Electric Co | Minnesota, Wisconsin, Kansas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 46.6594 | 58.1594 | 46.6594 | -28.25 | 0 | 28.25 | 69 | -15.25 | 69 | 15.25 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 57 | 6 | 68 | 12 | 57 | 6 | -28 | -3 | 0 | 0 | 28 | 3 | 68 | 12 | -15 | -3 | 68 | 12 | 15 | 3
3H7 | H frame | Public Service Company of New Mexico | New Mexico | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 49.1594 | 49.1594 | 49.1594 | -23.5 | 0 | 23.5 | 68.5 | -13.5 | 68.5 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 60 | 0 | 60 | 0 | 60 | 0 | -23 | -6 | 0 | 0 | 23 | 6 | 68 | 6 | -13.5 | 0 | 68 | 6 | 13.5 | 0
3H8 | H frame | Union electric company | Missouri, Nebraska, Minnesota | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 51.1594 | 51.1594 | 51.1594 | -24 | 0 | 24 | 72.5 | -26 | 72.5 | 26 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 62 | 0 | -24 | 0 | 0 | 0 | 24 | 0 | 72 | 6 | -26 | 0 | 72 | 6 | 26 | 0
3H9 | H frame | New Englad Electric System | New Englad, New Hampshire, Massachusets | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 52.6594 | 52.6594 | 52.6594 | -20 | 0 | 20 | 74.5 | -9.5 | 74.5 | 9.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 63 | 6 | 63 | 6 | 63 | 6 | -19 | -12 | 0 | 0 | 19 | 12 | 74 | 6 | -9 | -6 | 74 | 6 | 9 | 6
3H10 | H frame | Boston Edison Company | Massachusets | 2 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 96 | 70 | 70 | -10 | -32.75 | -10 | 111 | -27.25 | 111 | 27.25 | 96 | 70 | 70 | 10 | 10 | 32.75 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | -10 | 0 | -32 | -9 | -10 | 0 | 111 | 0 | -27 | -3 | 111 | 0 | 27 | 3 | 106.8406 | 0 | 80.8406 | 0 | 80.8406 | 0 | 10 | 0 | 10 | 0 | 32 | 9
3Y1 | Y | Tucson Gas & Electric Co | Arizona | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 109.2427 | 84.6594 | 84.6594 | 0 | -15 | 15 | 120.0833 | -13.5 | 120.0833 | 13.5 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 119 | 13 | 95 | 6 | 95 | 6 | 0 | 0 | -15 | 0 | 15 | 0 | 119 | 13 | -13.5 | 0 | 119 | 13 | 13.5 | 0
3Y2 | Y | Pacific Power Light corp |  | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -13.5 | 13.5 | 127 | -10 | 127 | 10 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -13 | -6 | 13 | 6 | 127 | 0 | -10 | 0 | 127 | 0 | 10 | 0
3Y3 | Y | SouthWestern electric company | Arkansas, Lousiana, Texas | 1 | 2 | 345 | 20 | 355 | 170 | 10.8406 | 116.1594 | 94.1594 | 94.1594 | 0 | -19.8333 | 19.8333 | 127 | -9 | 127 | 9 | -10.8406 | -10.8406 | -10.8406 | 0 | 0 | 0 | 127 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -19.5 | -4 | 19.5 | 4 | 127 | 0 | -9 | 0 | 127 | 0 | 9 | 0
5L1 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 96.7889 | 69.2889 | 69.2889 | 0 | -20 | 20 | 122.25 | -13 | 122.25 | 13 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 112 | 6 | 85 | 0 | 85 | 0 | 0 | 0 | -20 | 0 | 20 | 0 | 121 | 15 | -13 | 0 | 121 | 15 | 13 | 0
5L2 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 98.2889 | 69.2889 | 69.2889 | 0 | -15.3333 | 15.3333 | 121 | -12 | 121 | 12 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 114 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -15 | -4 | 15 | 4 | 121 | 0 | -12 | 0 | 121 | 0 | 12 | 0
5L3 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 90.2889 | 74.2889 | 74.2889 | 0 | -29 | 29 | 106 | -15 | 106 | 15 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 106 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | -29 | 0 | 29 | 0 | 106 | 0 | -15 | 0 | 106 | 0 | 15 | 0
5L4 | Lattice | Basin Electric Power Co-op | California, North Dakota, South Dakota, Colorado, Montana, New Mexico, Wyoming, Minnesota, Iowa | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 85 | 69.2889 | 69.2889 | 0 | -28 | 28 | 99 | -26 | 99 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 100.7111 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | -28 | 0 | 28 | 0 | 99 | 0 | -26 | 0 | 99 | 0 | 26 | 0
5L5 | Lattice | Carolina Power & Light Co | North Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 105 | 89.2889 | 89.2889 | 0 | -30.25 | 30.25 | 122.5 | -15.5 | 122.5 | 15.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120.7111 | 0 | 105 | 0 | 105 | 0 | 0 | 0 | -30 | -3 | 30 | 3 | 122 | 6 | -15.5 | 0 | 122 | 6 | 15.5 | 0
5L6 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 64.2889 | 64.2889 | 64.2889 | 0 | -35 | 35 | 95 | -25 | 95 | 25 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 95 | 0 | -25 | 0 | 95 | 0 | 25 | 0
5L7 | Lattice | Alabama Power Company, Baltimore Gas and Electric Company | Alabama, Maryland, | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -34 | 34 | 124 | -31 | 124 | 31 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -34 | 0 | 34 | 0 | 124 | 0 | -31 | 0 | 124 | 0 | 31 | 0
5L8 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -33 | 33 | 129 | -20 | 129 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -33 | 0 | 33 | 0 | 129 | 0 | -20 | 0 | 129 | 0 | 20 | 0
5L9 | Lattice | American Electric Power Co, Arizona Public Service Co, Duke Power Company | Virginia, Arizona, South Carolina | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 79.2889 | 79.2889 | 79.2889 | 0 | -32 | 32 | 109 | -24 | 109 | 24 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 95 | 0 | 95 | 0 | 95 | 0 | 0 | 0 | -32 | 0 | 32 | 0 | 109 | 0 | -24 | 0 | 109 | 0 | 24 | 0
5L10 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | 0 | -35 | 35 | 137 | -26 | 137 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | 0 | 0 | -35 | 0 | 35 | 0 | 137 | 0 | -26 | 0 | 137 | 0 | 26 | 0
5L11 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 100.2889 | 131.2889 | -15 | -25 | -15 | 172 | 0 | 0 | 0 | 131.2889 | 100.2889 | 69.2889 | 15 | 25 | 15 | 85 | 0 | 116 | 0 | 147 | 0 | -15 | 0 | -25 | 0 | -15 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 116 | 0 | 85 | 0 | 15 | 0 | 25 | 0 | 15 | 0
5L12 | Lattice | Bonneville Power Administration | Washington, Oregon, Idaho, Montana, Wyoming, Utah, Nevada, and California | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 114.2889 | 69.2889 | 69.2889 | -27.75 | -40.5 | -15 | 150 | -18.5 | 150 | 18.5 | 114.2889 | 69.2889 | 69.2889 | 27.75 | 15 | 40.5 | 130 | 0 | 85 | 0 | 85 | 0 | -27 | -9 | -40 | -6 | -15 | 0 | 150 | 0 | -18.5 | 0 | 150 | 0 | 18.5 | 0 | 130 | 0 | 85 | 0 | 85 | 0 | 27 | 9 | 15 | 0 | 40 | 6
5L13 | Lattice |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 112.2889 | 74.2889 | 74.2889 | -18.5 | -46.5 | -18.5 | 140 | -12.125 | 140 | 15.125 | 112.2889 | 74.2889 | 74.2889 | 18.5 | 18.5 | 46.5 | 128 | 0 | 90 | 0 | 90 | 0 | -18 | -6 | -46 | -6 | -18 | -6 | 140 | 0 | -12 | -1.5 | 140 | 0 | 15 | 1.5 | 128 | 0 | 90 | 0 | 90 | 0 | 18 | 6 | 18 | 6 | 46 | 6
5L14 | Lattice |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 94.2889 | 94.2889 | 94.2889 | -42 | 0 | 42 | 128 | -21.8333 | 128 | 21.8333 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -42 | 0 | 0 | 0 | 42 | 0 | 128 | 0 | -21 | -10 | 128 | 0 | 21 | 10
5P1 | Pole |  |  | 1 | 1 | 500 | 20 | 355 | 170 | 15.7111 | 69.2889 | 99.2889 | 129.2889 | 18 | 21 | 18 | 160 | 4 | 0 | 0 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 85 | 0 | 115 | 0 | 145 | 0 | 18 | 0 | 21 | 0 | 18 | 0 | 160 | 0 | 4 | 0 | 0 | 0 | 0 | 0
5P2 | Pole |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 60.7056 | 73.2889 | 85.7056 | 18 | -17 | 18 | 120 | -10 | 120 | 10 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 77 | -7 | 90 | -12 | 102 | -7 | 18 | 0 | -17 | 0 | 18 | 0 | 120 | 0 | -10 | 0 | 120 | 0 | 10 | 0
5H1 | H frame | Baltimore Gas and Electric Company, Baltimore Gas and Electric Company | Maryland, Maryland | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 104.2889 | 104.2889 | 104.2889 | -35 | 0 | 35 | 129 | -26 | 129 | 26 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 120 | 0 | -35 | 0 | 0 | 0 | 35 | 0 | 129 | 0 | -26 | 0 | 129 | 0 | 26 | 0
5H2 | H frame |  |  | 2 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 123 | 87 | 87 | -30 | -45 | -15 | 149 | -32 | 149 | 32 | 123 | 87 | 87 | 15 | 45 | 15 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | -30 | 0 | -45 | 0 | -15 | 0 | 149 | 0 | -32 | 0 | 149 | 0 | 32 | 0 | 138.7111 | 0 | 102.7111 | 0 | 102.7111 | 0 | 15 | 0 | 45 | 0 | 15 | 0
5Y1 | Y |  |  | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 106.25 | 139.25 | 106.25 | -21.5 | 0 | 21.5 | 153 | -13.75 | 153 | 13.75 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 122.7111 | -9 | 155.7111 | -9 | 122.7111 | -9 | -21 | -6 | 0 | 0 | 21 | 6 | 153 | 0 | -13 | -9 | 153 | 0 | 13 | 9
5Y2 | Y | Arkansas Power & Light Co. | Arkansas | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 118.5 | 88 | 88 | 0 | -21.5 | 21.5 | 131.5 | -20 | 131.5 | 20 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 133.7111 | 6 | 103.7111 | 0 | 103.7111 | 0 | 0 | 0 | -21 | -6 | 21 | 6 | 131 | 6 | -20 | 0 | 131 | 6 | 20 | 0
5Y3 | Y | Alabama Power Company | Alabama | 1 | 2 | 500 | 20 | 355 | 170 | 15.7111 | 151.25 | 126 | 126 | 0 | -21 | 21 | 165.25 | -17.5 | 165.25 | 17.5 | -15.7111 | -15.7111 | -15.7111 | 0 | 0 | 0 | 166.7111 | 3 | 141.7111 | 0 | 141.7111 | 0 | 0 | 0 | -21 | 0 | 21 | 0 | 165 | 3 | -17 | -6 | 165 | 3 | 17 | 6
7L1 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 92 | 92 | 92 | -44.5 | 0 | 44.5 | 127 | -36 | 127 | 36 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 115.0953 | 0 | 115.0953 | 0 | 115.0953 | 0 | -44 | -6 | 0 | 0 | 44 | 6 | 127 | 0 | -36 | 0 | 127 | 0 | 36 | 0
7L2 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 86.9047 | 86.9047 | 86.9047 | -45 | 0 | 45 | 138.6667 | -50 | 138.6667 | 50 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 110 | 0 | -45 | 0 | 0 | 0 | 45 | 0 | 138 | 8 | -50 | 0 | 138 | 8 | 50 | 0
7L3 | Lattice |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 135 | 135 | 135 | -41.8333 | 0 | 41.8333 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 158.0953 | 0 | 158.0953 | 0 | 158.0953 | 0 | -41 | -10 | 0 | 0 | 41 | 10 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7P1 | Pole |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 100.9047 | 100.9047 | 100.9047 | -39.3333 | 0 | 39.3333 | 145 | -66 | 145 | 66 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 124 | 0 | 124 | 0 | 124 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 145 | 0 | -66 | 0 | 145 | 0 | 66 | 0
7H1 | H frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 131 | 131 | 131 | -50 | 0 | 50 | 175 | -30 | 175 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 154.0953 | 0 | 154.0953 | 0 | 154.0953 | 0 | -50 | 0 | 0 | 0 | 50 | 0 | 175 | 0 | -30 | 0 | 175 | 0 | 30 | 0
7V1 | V frame |  |  | 1 | 2 | 735 | 20 | 355 | 170 | 23.0953 | 110 | 110 | 110 | -39.3333 | 0 | 39.3333 | 150 | -30 | 150 | 30 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 133.0953 | 0 | 133.0953 | 0 | 133.0953 | 0 | -39 | -4 | 0 | 0 | 39 | 4 | 150 | 0 | -30 | 0 | 150 | 0 | 30 | 0
DC1 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0
DC2 | [5 empty] | 735 | 20 | 355 | 170 | 23.0953 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.0953 | -23.0953 | -23.0953 | 0 | 0 | 0